## Slide 1: NAWI RO Analysis Progress Report
W. Kumagai, H. Soya, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
June 22th, 2023
SGDC

## Slide 2: Self Introduction
Name
  Hiroaki Soya
Entering year
  2018
Department
  MK HQ INV Pjt Design Dept. Operational Excellence Gr.
  Supervisor : Kamada-san
Specialty
  Control Engineering

## Slide 3: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 4: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion

## Slide 5
3 Stages configuration and Toray’s TM720-370 is deployed
  Data period is three years from 2020 to 2023.
  Provided minute interval data were converted to 30minutes trends.
RO
UF
Potable Water
UV／AOP
1. RO Permeate Water Quality Prediction
Overall view of RO system / Water Quality Model Prediction Targets
RO system
measuring point
P
pump
Target①
Target②
Target③
Target④
RO Permeate Water Quality Prediction targets are Target①~④

## Slide 6
We use the Multiple Linear Regression Model and the following variables:
Target number | Target① | Target② | Target③ | Target④
 | Stage1 Permeate EC | Stage2 Permeate EC | Stage3 Permeate EC | Permeate TOC
RO Stage 1 Feed Pressure | X |  |  | X
RO Feed EC | X |  |  | X
RO Feed Flow* | X |  |  | X
RO Feed Temperature | X | X | X | X
RO Feed pH | X |  |  | X
UF Filtrate Total Chlorine | X | X | X | X
RO Stage 2 Feed EC* |  | X |  | 
RO Stage 2 Feed Flow* |  | X |  | 
RO Stage 3 Feed Pressure |  |  | X | X
RO Stage 3 Feed EC* |  |  | X | 
RO Stage 3 Feed Flow* |  |  | X | 
RO Feed TOC |  |  |  | X
Water Quality Model Details
1. RO Permeate Water Quality Prediction
EC = Electric Conductivity, *Calculation Tag
Water Quality Model
Output
Y
Input
X
Output Y
Input X

## Slide 7
Focused Period ：July 1st, 2021 ~ July 27th, 2022
Continuous Chain Evaluation (1 week Training and 1 week Prediction)
Data Preprocessing
  Removing Outliers
  Noisy Data Imputation
  Missing Data Imputation
Term | Training Period | Prediction Period
1 | from July 1st to July 7th, 2021 | from July 8th to July 14th, 2021
2 | from July 8th to July 14th, 2021 | from July 15th to July 21st, 2021
54 | from July 7th to July 13th, 2022 | from July 14th to July 20th, 2022
55 | from July 14th to July 20th, 2022 | from July 21st to July 27th, 2022
Term | Training Period | Prediction Period
1 | from July 1st to July 7th, 2021 | from July 8th to July 14th, 2021
2 | from July 8th to July 14th, 2021 | from July 15th to July 21st, 2021
54 | from July 7th to July 13th, 2022 | from July 14th to July 20th, 2022
55 | from July 14th to July 20th, 2022 | from July 21st to July 27th, 2022
Conditions for Modeling
1. RO Permeate Water Quality Prediction

## Slide 8
Index | Stage1 Permeate EC
RMSE | 2.07 [uS/cm]
MAPE | 5.27 [%]
1. RO Permeate Water Quality Prediction
Result：①Stage1 Permeate EC and ②Stage2 Permeate EC
Index | Stage2 Permeate EC
RMSE | 2.36 [uS/cm]
MAPE | 5.04 [%]
Pre-processed actual data
Predicted data
Pre-processed actual data
Predicted data
Target 1: Stage 1 Permeate EC
Target 2: Stage 2 Permeate EC

## Slide 9
Index | Stage3 Permeate EC
RMSE | 4.63 [uS/cm]
MAPE | 9.04 [%]
1. RO Permeate Water Quality Prediction
Result：③Stage3 Permeate EC and ④Permeate TOC
Index | Permeate TOC
RMSE | 0.030 [mg/L]
MAPE | 19.46 [%]
Pre-processed actual data
Predicted data
Pre-processed actual data
Predicted data
Target 3: Stage 3 Permeate EC
Target 4: Permeate TOC

## Slide 10
Good prediction for regular fluctuation except Permeate TOC.
1. RO Permeate Water Quality Prediction
Result： Enlargement instances for a week (July 29th ~ August 5th, 2021)
Target 1: Stage 1 Permeate EC
Target 2: Stage 2 Permeate EC
Target 3: Stage 3 Permeate EC
Target 4: Permeate TOC

## Slide 11
  Issue
  Immature treatment of outliers Spike noise frequently are particularly observed in permeate TOC data.
  Action
  Implementation of other outlier handling methods
  Confirmation of the detection limits and sensitivity of the Measuring instrument
1. RO Permeate Water Quality Prediction
Future Tasks

## Slide 12: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 13: 2. RO Membrane Fouling Modeling Targeting
Clogging Classification
  Scaling: Chemical & Fluidic dynamics
  Fouling: Bio & Fluidic dynamics
https://www.ourpureh2o.com/home/showpublisheddocument/14305/637964028619970000
scaling
fouling

## Slide 14: 2. RO Membrane Fouling Modeling Physical Dynamics based Modeling
Theory：Bernoulli's principle
https://www.vedantu.com/physics/bernoullis-theorem

## Slide 15: 2. RO Membrane Fouling Modeling Physical Dynamics based Modeling
Definition of system input and output

## Slide 16: 2. RO Membrane Fouling Modeling Application to LVMWD
Bernoulli's Principle
  Exchanging volume flow to velocity
  Bernoulli’s principle at RO System
energy loss fouling?
Future work：Considering fluid of mass at each pipes and booster pumps dynamics

## Slide 17: 2. RO Membrane Fouling Modeling Modeling
Step1 : Estimate ρ,A from data
  Estimate using least squares
LVMWD
OCWD
measured
measured
calc
(equation of continuity)
Estimating
Estimating
Estimating only “”
  Notes
  system of units converting to the SI unit system e.g. Flow Rate : [gpm] to [m^3/s]
  Preprocessing using 12 [hour] moving average

## Slide 18: 2. RO Membrane Fouling Modeling Modeling
Step2 : Calculate
  Calculate using
  Normalize into 0-1
estimated
calc & measured

## Slide 19: 2. RO Membrane Fouling Modeling Future Tasks
Modeling Dynamics
  including the followings in Bernoulli's principle
    Buster Pump dynamics
    Calculating Area of each pipes using P&ID data
  Focus to 1st stage RO membrane
    Fouling is mainly occurred at 1st Stage
SV vs
  Formulating the relationship between the estimated and the input of chlorine(SV) in order to optimize operation.
https://www.n-pipe.com/schedule-80-stainless-steel-pipe-dimensions-thickness.html

## Slide 20: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 21: Scheduling Optimization
RO optimization problem is formulated into a scheduling optimization.
The procedure consists of below steps.
3. RO Optimization Concept
A
B
C
Facility Model
: Optimization Variable
1. Drawing Flow Chart
(Operational Cost)
(Facility Characteristics)
2. Formulation
Optimization Problem
Time
Operational Cost is $XX.
3. Calculation
Operational Schedule
Sample Flow Chart

## Slide 22: Flow Chart for RO Optimization
3. RO Optimization Concept > Flow Chart
We define the flow chart, variables, mathematical models.
RO Whole Part
RO Each Stage Part

## Slide 23: Variable List
3. RO Optimization Concept > Problem Formulation
Family | ID No. | Description | Variable / Param
RO Feed | ID000 | UF Filtrate Total Chlorine | Opt. Variable
RO Feed | ID001 | S1 Feed EC | Fixed Parameter
RO Feed | ID002 | S1 Feed TOC | Fixed Parameter
RO Feed | ID003 | Feed Temperature | Fixed Parameter
RO Feed | ID004 | Feed pH | Fixed Parameter
RO Stage1 | ID100 | S1 Feed Pressure | Fixed Parameter
RO Stage1 | ID101 | S1 Feed Flow Rate | Fixed Parameter
RO Stage1 | ID102 | S1 Permeate Flow Rate | Fixed Parameter
RO Stage2 | ID200 | S2 Feed Flow Rate | Fixed Parameter
RO Stage2 | ID201 | S2 Permeate Flow Rate | Fixed Parameter
RO Stage3 | ID300 | S3 Feed Pressure | Fixed Parameter
RO Stage3 | ID301 | S3 Feed Flow Rate | Fixed Parameter
RO Stage1 | ID1000 | S1 Permeate EC | Intermediate Variable
RO Stage2 | ID2000 | S2 Feed EC | Intermediate Variable
RO Stage2 | ID2001 | S2 Permeate EC | Intermediate Variable
RO Stage3 | ID3000 | S3 Feed EC | Intermediate Variable
RO Stage3 | ID3001 | S3 Permeate EC | Intermediate Variable
RO Total | ID4000 | Permeate TOC | Intermediate Variable
Chemical Dosing Cost
Calculated by Mathematical Model

## Slide 24: Optimization Problem
3. RO Optimization Concept > Problem Formulation
Objective Function
Main Constraint Conditions
Water Quality Standards and Upper / Lower limit
Logarithmic Reduction Value (LRV):
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Stage 1 Permeate EC LRV | - | 1 | 2.5
Stage 2 Permeate EC LRV | - | 1 | 2.5
Stage 3 Permeate EC LRV | - | 1 | 2.5
Permeate TOC LRV | - | 1 | 2.0
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Stage 1 Permeate EC LRV | - | 1 | 2.5
Stage 2 Permeate EC LRV | - | 1 | 2.5
Stage 3 Permeate EC LRV | - | 1 | 2.5
Permeate TOC LRV | - | 1 | 2.0
are calculated by the prediction model at the previous part.
UF Filtrate Total Chlorine
Minimizing chemical cost while satisfying water quality standards.

## Slide 25: Question (SGDC to INV)
3. Q&A / Discussion

## Slide 27: Supplementary Physical Dynamics based Modeling
Using Data
[mg/L Cl2]
RO Feed Free Chlorine
[mg/L Cl2]
UF Filtrate Total Chlorine
RO Stage 3 Concentrate Pressue
[psi]
RO Stage 3 Concentrate Flow
[psi]
[gpm]
RO Stage 1 Feed Pressure

## Slide 28: Difference per Objective
Step up from (small, easy) to (large, difficult).
Optimization effect
Small
Middle
Large
Optimization period
Short-term
(minutes to hours)
Mid-term
(days to months)
Long-term
(months to years)
Model strategy
Closer to statistical models
Statistical/ Physical Models
Closer to the physical model
Difficulty
Easy
Middle
Difficult
(1) 最終水質と供給量を考慮
(2) RO膜閉塞状態も考慮
(3) RO膜劣化も考慮
(1) Consider water quality and flow rate in Post-RO
(2) Consider RO Clogging
(3) Consider RO Deterioration
Supplementary: RO Analytical Policy
Notes: This slide shows the procedure of RO analysis. We plan to step up from small and easy to large and difficult. There are two reasons. First reason is time-span and period in optimization. Second reason is model strategy.

## Slide 29
[psi]
[psi]
[psi]
Supplementary: LVMWD Data RO Analysis
Pressure Trend (Feed)

## Slide 30
30
[psi]
[psi]
[psi]
[psi]
[psi]
Supplementary: LVMWD Data RO Analysis
Pressure Trend (Permeate, 2nd and 3rd Stage Concentrate)

## Slide 31
31
[gpm]
[gpm]
RO Stage Feed Flow Rate [gpm]
1
Supplementary: LVMWD Data RO Analysis
Flow Rate Trend (Feed)

## Slide 32
32
Supplementary: LVMWD Data RO Analysis
Flow Rate Trend (Permeate)
RO Stage Permeate Flow Rate [gpm]
1
RO Stage Permeate Flow Rate [gpm]
2
RO Stage Permeate Flow Rate [gpm]
3