## Slide 1: NAWI RO Analysis Progress Report
W. Kumagai, H. Soya, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
August 30th, 2023
SGDC

## Slide 2: Agenda
RO Data Analysis and Optimization
RO Permeate Water Quality Prediction
RO Optimization Simulation
RO Membrane Scaling Modeling
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 3: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion

## Slide 4
3 Stages configuration and Toray’s TM720-370 is deployed
  Data period is three years from 2020 to 2023.
  Provided minute interval data were converted to 30minutes trends.
RO
UF
Potable Water
UV／AOP
1. RO Permeate Water Quality Prediction
Overall view of RO system / Water Quality Model Prediction Targets
RO system
measuring point
P
pump
Target①
Target②
Target③
Target④
RO Permeate Water Quality Prediction targets are Target①~④

## Slide 5
We use the Multiple Linear Regression Model and the following variables:
Target number | Target① | Target② | Target③ | Target④
 | Stage1 Permeate EC | Stage2 Permeate EC | Stage3 Permeate EC | Permeate TOC
RO Stage 1 Feed Pressure | X |  |  | X
RO Feed EC | X |  |  | X
RO Feed Flow* | X |  |  | X
RO Feed Temperature | X | X | X | X
RO Feed pH | X |  |  | X
UF Filtrate Total Chlorine | X | X | X | X
RO Stage 2 Feed EC* |  | X |  | 
RO Stage 2 Feed Flow* |  | X |  | 
RO Stage 3 Feed Pressure |  |  | X | X
RO Stage 3 Feed EC* |  |  | X | 
RO Stage 3 Feed Flow* |  |  | X | 
RO Feed TOC |  |  |  | X
Water Quality Model Details
1. RO Permeate Water Quality Prediction
EC = Electric Conductivity, *Calculation Tag
Water Quality Model
Output
Y
Input
X
Output Y
Input X

## Slide 6
Focused Period ：July 1st, 2021 ~ July 27th, 2022
Continuous Chain Evaluation (1 week Training and 1 week Prediction)
Data Preprocessing
  Removing Outliers
  Noisy Data Imputation
  Missing Data Imputation
Term | Training Period | Prediction Period
1 | from July 1st to July 7th, 2021 | from July 8th to July 14th, 2021
2 | from July 8th to July 14th, 2021 | from July 15th to July 21st, 2021
54 | from July 7th to July 13th, 2022 | from July 14th to July 20th, 2022
55 | from July 14th to July 20th, 2022 | from July 21st to July 27th, 2022
Term | Training Period | Prediction Period
1 | from July 1st to July 7th, 2021 | from July 8th to July 14th, 2021
2 | from July 8th to July 14th, 2021 | from July 15th to July 21st, 2021
54 | from July 7th to July 13th, 2022 | from July 14th to July 20th, 2022
55 | from July 14th to July 20th, 2022 | from July 21st to July 27th, 2022
Conditions for Modeling
1. RO Permeate Water Quality Prediction

## Slide 7
Index | Stage1 Permeate EC
RMSE | 2.07 [uS/cm]
MAPE | 5.27 [%]
1. RO Permeate Water Quality Prediction
Result：①Stage1 Permeate EC and ②Stage2 Permeate EC
Index | Stage2 Permeate EC
RMSE | 2.36 [uS/cm]
MAPE | 5.04 [%]
Pre-processed actual data
Predicted data
Pre-processed actual data
Predicted data
Target 1: Stage 1 Permeate EC
Target 2: Stage 2 Permeate EC

## Slide 8
Index | Stage3 Permeate EC
RMSE | 4.63 [uS/cm]
MAPE | 9.04 [%]
1. RO Permeate Water Quality Prediction
Result：③Stage3 Permeate EC and ④Permeate TOC
Index | Permeate TOC
RMSE | 0.030 [mg/L]
MAPE | 19.46 [%]
Pre-processed actual data
Predicted data
Pre-processed actual data
Predicted data
Target 3: Stage 3 Permeate EC
Target 4: Permeate TOC

## Slide 9
Good prediction for regular fluctuation except Permeate TOC.
1. RO Permeate Water Quality Prediction
Result： Enlargement instances for a week (July 29th ~ August 5th, 2021)
Target 1: Stage 1 Permeate EC
Target 2: Stage 2 Permeate EC
Target 3: Stage 3 Permeate EC
Target 4: Permeate TOC

## Slide 10
  Issue
  Immature treatment of outliers Spike noise frequently are particularly observed in permeate TOC data.
  Action
  Implementation of other outlier handling methods
  Confirmation of the detection limits and sensitivity of the Measuring instrument
1. RO Permeate Water Quality Prediction
Future Tasks

## Slide 11: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 12: 2. RO Membrane Fouling Modeling Targeting
Clogging Classification
  Scaling: Chemical & Fluidic dynamics
  Fouling: Bio & Fluidic dynamics
https://www.ourpureh2o.com/home/showpublisheddocument/14305/637964028619970000
scaling
fouling

## Slide 13: 2. RO Membrane Fouling Modeling Physical Dynamics based Modeling
Theory：Bernoulli's principle
https://www.vedantu.com/physics/bernoullis-theorem

## Slide 14: 2. RO Membrane Fouling Modeling Physical Dynamics based Modeling
Definition of system input and output

## Slide 15: 2. RO Membrane Fouling Modeling Application to LVMWD
Bernoulli's Principle
  Exchanging volume flow to velocity
  Bernoulli’s principle at RO System
energy loss fouling?
Future work：Considering fluid of mass at each pipes and booster pumps dynamics

## Slide 16: 2. RO Membrane Fouling Modeling Modeling
Step1 : Estimate ρ,A from data
  Estimate using least squares
LVMWD
OCWD
measured
measured
calc
(equation of continuity)
Estimating
Estimating
Estimating only “”
  Notes
  system of units converting to the SI unit system e.g. Flow Rate : [gpm] to [m^3/s]
  Preprocessing using 12 [hour] moving average

## Slide 17: 2. RO Membrane Fouling Modeling Modeling
Step2 : Calculate
  Calculate using
  Normalize into 0-1
estimated
calc & measured

## Slide 18: 2. RO Membrane Fouling Modeling Future Tasks
Modeling Dynamics
  including the followings in Bernoulli's principle
    Buster Pump dynamics
    Calculating Area of each pipes using P&ID data
  Focus to 1st stage RO membrane
    Fouling is mainly occurred at 1st Stage
SV vs
  Formulating the relationship between the estimated and the input of chlorine(SV) in order to optimize operation.
https://www.n-pipe.com/schedule-80-stainless-steel-pipe-dimensions-thickness.html

## Slide 19: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: Next part is RO Optimization Concept.

## Slide 20: Plant Scheduling Optimization
RO optimization problem is formulated into a scheduling optimization.
The procedure consists of the following steps.
3. RO Optimization Concept
A
B
C
Facility Model
: Optimization Variable
1. Drawing Flow Chart
(Operational Cost)
(Facility Characteristics)
2. Formulation
Optimization Problem
Time
Operational Cost is $XX.
3. Calculation
Operational Schedule
Sample Flow Chart
Notes: RO optimization problem is formulated into a plant scheduling optimization. The procedure~. First step is drawing flow chart. In this chart, arrows connecting objects are assigned optimization variables. The object plays the role of exogenous variable, mathematical model, and predictive variable. Second step is formulation optimization problem. I define the minimizing the objective function and the constraints. Third step is calculation operational schedule. I solve the formulated problem using optimization algorithm.

## Slide 21: Flow Chart for RO Optimization
3. RO Optimization Concept > Flow Chart
We define the flow chart, variables, mathematical models.
RO Whole Part
RO Each Stage Part
Exogenous Variable
Predictive Variable
(water quality)
Mathematical Model
(prediction model)
Notes: This is the flow chart for Las Virgenes model. I divided into the RO whole part and RO each stage part. The storage object is exogenous variable and the square object is predictive variable that is water quality. The hexagon object is mathematical model and have both input and output variable. The arrow toward the object is input variable and the arrow from the object is output variable. Especially, the four objects enclosed in the square are the prediction model constructed by Imoto-san.

## Slide 22: Optimization Problem
3. RO Optimization Concept > Problem Formulation
Objective Function
Main Constraint Conditions
Water Quality Standards and Upper / Lower limit
Logarithmic Reduction Value (LRV):
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Stage 1 EC LRV | - | 1 | 2.5
Stage 2 EC LRV | - | 1 | 2.5
Stage 3 EC LRV | - | 1 | 2.5
TOC LRV | - | 1 | 2.0
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Stage 1 EC LRV | - | 1 | 2.5
Stage 2 EC LRV | - | 1 | 2.5
Stage 3 EC LRV | - | 1 | 2.5
TOC LRV | - | 1 | 2.0
are calculated by the prediction model at the previous part.
UF Filtrate Total Chlorine
Minimizing chemical cost while satisfying water quality standards.
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 23: Module Configuration
2. 構成
pkg
main.py
Optimization Module
Optimization Problem
model
params
Definition objective and constraint functions
import_model.py
Water quality Prediction module
Optimization Problem Definition
Optimization Solver Definition
unit_algorithm.py
algorithms
Definition objective and constraint functions
import given model files from outside

## Slide 24: Calculate Schedule
3. RO Optimization Concept > Calculate Schedule
Future task is to solve schedule problem and introduce the fouling model.
  I’m writing the python code from scratch.
We must select the optimization algorithm the problem class.
  This problem class can be nonlinear or black-box optimization in future efforts of modeling.
Therefore, we will use the combined algorithm with SHADE and the feasibility rule.
  They are classified as metaheuristic algorithm as well as Genetic Algorithm.
  SHADE is the state-of-the-art solver in the black-box optimization field.

## Slide 25: Question (SGDC to INV)
3. Q&A / Discussion

## Slide 26: 概要
1か月評価のための期間選定と効果試算をする。
膜詰まりモデリングのために、差圧を入れて、クラスタ分析の続きを実施する。
個人目的
今週進捗
来週目標
Task1のための最適化モデルを構築し、効果試算を実施する。
Task2を見据えた最適化システム構成案を検討する。
データを変更して、RO最適化シミュレーションを再実行した。

## Slide 27: My Task in NAWI Task1
Develop the RO optimization simulator with new optimizer built in, not based on DDMO.
  It assumes that Yokogawa engineer can use it although it has not yet been fully tested.
  It needs more functions for pilot/demo-scale implementation in NAWI Task2.
Estimate the optimization effect comparing operational cost.
1. RO Optimization Simulator

## Slide 28: Functional Configuration of RO Optimization Simulator
1. RO Optimization Simulator
Preprocessing
Generate Model
Generate Param
Validate Problem
Optimize
Unify the file format, e.g., add calculated tag and up/down resampling according to given timespan based on master data without outliers.
Postprocessing
Generate optimization / prediction model files with user-specified modeling using data in the training period.
Generate the parameter file for optimization using data in the optimization period.
Calculate prediction model error by input optimization variables fixed to actual value into optimization model, i.e., predict validation.
Solve the RO plant scheduling problem by optimizer.
Calculate each average value and LRV of water quality, and draw each variable trend chart including LRV.

## Slide 29: 透過水質
トレンドを大まかに捉えている。
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
2.1 LVMWD > 1st week 予測結果
Blue: Actual / Orange: Prediction
Actual Ave.: 0.067 [mg/L],
Predict Ave.: 0.064 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Predict Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Predict Ave.: 2.03
Actual Ave.: 1.83,
Predict Ave.: 1.83

## Slide 30: 探索結果（最良解の推移）
実行可能解を得て、コストを改善する解が得られている。
2.1 LVMWD > 1st week 最適化結果
10,000の半分で止めた
Blue: Objective Function Value /
Orange: Constraint Violation
約10分

## Slide 31: 操作計画：コスト変数と固定変数
UF Total Chlorine [mg/L]（コスト）
S1流入圧力 [psi]（固定）
S1流入量 [gpm]（固定）
S1流入EC [uS/cm]（固定）
流入TOC [mg/L]（固定）
2.1 LVMWD > 1st week 最適化結果
探索途中だが、コスト削減する解となっている。
Blue: Actual / Orange: Optimized
Actual Ave.: 0.40 [mg/L],
Optimized Ave.: 0.38 [mg/L]

## Slide 32: 操作計画：透過水質
Actual Ave.: 0.067 [mg/L],
Optimized Ave.: 0.063 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Optimized Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Optimized Ave.: 2.03
Actual Ave.: 1.83,
Optimized Ave.: 1.83
LRV基準を守る範囲で、微小に変化している。
2.1 LVMWD > 1st week 最適化結果
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]

## Slide 33: コスト換算
この問題設定や条件では、ほぼ改善の余地が無いと見積もれる。
  ただ、若干改善が停滞気味なので、何らかの制約に課されて改善できない可能性もある
2.1 LVMWD > 1st week 効果試算
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err.
Total Chlorine [mg/L] | 0.40 | 0.38 | - 0.02 |  | - 0.02
EC [uS/cm] | 20.76 | 20.87 | + 0.11 | + 0.11 | - 0.0004
TOC [mg/L] | 0.067 | 0.063 | - 0.004 | - 0.004 | + 0.0004
LRV EC | 1.83 | 1.82 | - 0.01 | - 0.01 | + 0.002
LRV TOC | 2.01 | 2.03 | + 0.02 | + 0.02 | + 0.003

## Slide 34: 透過水質
トレンドを大まかに捉えているが、ECの予測値が実績よりも若干低い。
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
2.2 OCWD > 1st week 予測結果
Blue: Actual / Orange: Prediction
Actual Ave.: 0.055 [ppm],
Predict Ave.: 0.052 [ppm]
Actual Ave.: 23.48 [uS/cm],
Predict Ave.: 18.61 [uS/cm]
Actual Ave.: 2.22,
Predict Ave.: 2.24
Actual Ave.: 1.88,
Predict Ave.: 1.99

## Slide 35: 探索結果（最良解の推移）
実行可能解を得て、コストを改善する解が得られている。
2.2 OCWD > 1st week 最適化結果
10,000の半分で止めた
Blue: Objective Function Value /
Orange: Constraint Violation
約9分

## Slide 36: 操作計画：コスト変数と固定変数
Sulfuric Acid [ton/hour]（コスト）
S1流入圧力 [psi]（固定）
S1流入量 [gpm]（固定）
S1流入EC [uS/cm]（固定）
流入TOC [ppm]（固定）
Inhibitor [ton/hour] （コスト）
2.2 OCWD > 1st week 最適化結果
LRV基準の制約によって、Inhibitorが実績とほぼ同じ値になっている。
Blue: Actual / Orange: Optimized
Actual Ave.: 0.39 [ton/hour],
Optimized Ave.: 0.38 [ton/hour]
Actual Ave.: 0.0559 [ton/hour],
Optimized Ave.: 0.0560 [ton/hour]

## Slide 37: 操作計画：透過水質
ECのLRV基準の上限に位置する解となっている。
2.2 OCWD > 1st week 最適化結果
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
Actual Ave.: 0.055 [ppm],
Optimized Ave.: 0.053 [ppm]
Actual Ave.: 23.5 [uS/cm],
Optimized Ave.: 18.7 [uS/cm]
Actual Ave.: 2.22,
Optimized Ave.: 2.23
Actual Ave.: 1.88,
Optimized Ave.: 1.98

## Slide 38: コスト換算
約47$/day(18K$/year, 2.5M\/year)の削減効果と見積もれる。
  ただし、この条件では、ほぼ改善の余地が無いと見積もれる。
2.2 OCWD > 1st week 最適化結果
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err. | Cost [$/day]
Acid [ton/hour] | 0.39 | 0.38 | - 0.009 |  | - 0.009 | - 53.3
Inhibitor [ton/hour] | 0.0559 | 0.0560 | + 0.0001 |  | + 0.0001 | + 6.22
EC [uS/cm] | 23.5 | 18.7 | - 4.74 | - 4.87 | + 0.13 | 
TOC [mg/L] | 0.055 | 0.053 | - 0.002 | - 0.003 | + 0.001 | 
LRV EC | 1.88 | 1.98 | + 0.30 | - 0.01 | - 0.003 | 
LRV TOC | 2.217 | 2.234 | + 0.02 | + 0.02 | - 0.005 | 
Total |  |  |  |  |  | - 47.1

## Slide 39: 課題１
各週評価に基づく1か月間の効果試算
  方式：1週間学習＆1週間最適化を、5週実施
  LVMWD：2022/3/14～2022/3/21（2022/4/22までは計算中）
  OCWD：2022/5/20～2022/6/24
薬液と水質の関係が実際と解離しない期間における効果試算
  現在の評価期間では、実際と矛盾する方向に最適化している
3. 今後の課題

## Slide 40: 課題２
長期予測のためのRFモデルを組み込んだ最適化計算
  予測モデルをRFで代替したが、解の評価に時間がかかりすぎて、同様の最適化計算が現実的ではなかった。
  MLRを使った最適化計算時間は約20min、RFの場合は約6,200min（103hour）で、MLRの約300倍の時間を要すると見積もられる。
  理論的な計算量から考えると、妥当な計算時間なので、C#プログラムを使っても厳しいと予想される。
    ライブラリ “pythonnet”を使えば、C#のdllや.NETを呼び出せる
3. 今後の課題

## Slide 41: 課題３
膜詰まりモデル構築
  現状のLVMWDの最適化シミュレーションの設定では、客先に最適化効果を主張できそうなものはほぼないと考えられる。
  クラスタリングから、差圧と導電率の関係からCIPとの関連性を見出せそうなことはわかったが、CIP区間毎で大きく異なる運転をしている疑いがあるため、これ以上の解析は期待できない。
  最適化計算環境を優先しているため、井本さんに依頼している。
3. 今後の課題

## Slide 42: 状況
精緻な長期最適化の前に、膜閉塞分析の結論を優先すべき。
3. 今後の課題
薬品
膜閉塞度
膜閉塞度
水質
薬品
水質
水質予測モデル
膜閉塞モデル
1週間 最適化
1か月間 最適化＆効果試算
運転実績データ
最適化モデル
？
机上FSの流れ

## Slide 44: [LVMWD] RO System Configuration and Measurement Points
P
・Feed Free Chlorine
・Feed Conductivity
・Feed pH, TOC, Temp
・Feed Pressure
・Feed Flow (Calc)
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Combined Permeate TOC
・Combined Permeate Conductivity
・Concentrate Pressure
・Concentrate Flow
・Inlet Free Chlorine
・Inlet Total Chlorine
・Inlet pH
・Inlet UVT
・Inlet Flow
UV
・Outlet Free Chlorine
・Outlet Total Chlorine
・Inlet UVT
・UV Dose
・UV Intensity
・UV Lamp Power (Constant 50%)
RO 1st Stage
RO 2nd Stage
RO 3rd Stage
Feed Pressure
Concentrate Pressure
Feed Pressure
P
This pump decides the feed flow to RO.
a
b
c
d
e
<Differential Pressure>
Stage 1 = －
Stage 2 = －
Stage 3 = －
a
b
b
c
d
e