## Slide 1: NAWI RO Analysis Progress Report
W. Kumagai, H. Soya, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
August 30th, 2023
SGDC

## Slide 2: Agenda
RO Operation Optimization
RO Permeate Water Quality Prediction / Q&A
RO Optimization Simulation / Q&A
RO Membrane Scaling Modeling / Q&A
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 3: Objective of RO Optimization
Chemical dosing costs are minimized considering RO membrane condition within the range of maintaining water quality and flow rate.
  Maintaining high recovery rate, good water quality (high salt rejection), and extending RO membrane life.
  Considering water quality, permeate flow rate, and RO clogging status.
RO
NaClO
UF
Sulfuric Acid／Anti-Scalant
Potable Water
UV / AOP
UV Radiation with H2O2 or NaClO
Water quality
Degree of Clogging
Membrane cleaning
Membrane life
1. RO Operation Optimization
Given Region
Given Region
Subject to be optimization target if interchangeable with RO.
Chemical costs
Chemical costs
Water quality and flow rate to be maintained
Clogging due to fouling Scaling by crystallization Bio-fouling by deposit
Notes: First, I explain RO data analysis and optimization policy. This shows potable water reuse process. Water from sewage plant is treated by this process and supplied to potable reuse.
It mainly consists of UF, RO, UV, and AOP process units. The objective of RO optimization shows operating costs are ~. There are important costs in many places, for example, chemical cost, RO membrane cleaning cost, and electricity cost. Moreover there are considering conditions in many places, for example, recover rate, water quality, and RO membrane life. So, optimization strategy is to select critical costs and conditions according to priority.
Based on the stages, RO analytical policy is to expand the control and considered value step by step. First stage is to control and consider yellow values. Green values are added in second stage and red values are added in third stage as well. But, gray regions are considered as given area in RO optimization, so they are fixed to actual value when calculation.

## Slide 4
3 Stages configuration.
Water quality data is RO permeate TOC and Conductivity.
  Monitoring LRV (logarithmic reduce value) as water-quality standards.
1. RO Operation Optimization
Overall view of LVMWD RO system
RO system
measuring point
P
pump
Water Quality Targets are shown in red.

## Slide 5: Plant Scheduling Optimization
RO optimization problem is formulated into a scheduling optimization.
The procedure consists of the following steps.
1. RO Operation Optimization
A
B
C
Facility Model
: Optimization Variable
1. Drawing Flow Chart
(Operational Cost)
(Facility Characteristics)
2. Formulation
Optimization Problem
Time
Operational Cost is $XX.
3. Calculation
Operational Schedule
Sample Flow Chart
Notes: RO optimization problem is formulated into a plant scheduling optimization. The procedure~. First step is drawing flow chart. In this chart, arrows connecting objects are assigned optimization variables. The object plays the role of exogenous variable, mathematical model, and predictive variable. Second step is formulation optimization problem. I define the minimizing the objective function and the constraints. Third step is calculation operational schedule. I solve the formulated problem using optimization algorithm.

## Slide 6: Desktop Evaluation Flow Chart
1. RO Operation Optimization
Calculate the optimization effect
Plant Info. Check
Step1
Model Construction
Step2
Step3
Optimization
Effect Calculation
Check the plant flow & data
Step4
Construct and validate the plant model
Execute optimization simulation
Check the plant flow chart, control & manipulated variable, evaluation index, and data trends.
Decide optimization story and modeling way.
Construct the plant model including water quality prediction models.
Especially prediction models are validated individually.
Implement the optimization problem and optimizer.
Execute simulation and validate/check the behavior.
Compare optimization results with operation actual data in the past.
Detailed in Section 2
Detailed in Section 3
Notes: We have taken the following chart.

## Slide 7: Agenda
RO Operation Optimization
RO Permeate Water Quality Prediction / Q&A
RO Optimization Simulation / Q&A
RO Membrane Scaling Modeling / Q&A
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 8: Today’s Topic Agenda
2. RO Permeate Water Quality Prediction
2.1 Introduction: summary up to the previous meeting
  Data Preprocessing, Prediction model
2.2 Prediction and Preprocessing Results
  Prediction by Multiple Regression Model and Random Forest
  Minor Manual Preprocessing for Permeate TOC Data

## Slide 9: Data Preprocessing
  Creating “master data“ for analysis from raw dataset by pretreatment.
  Step1: Local Rule based Filtering
    Getting rid of the data during the period as the following three rules.
  Step2: Systematic Rule based Filtering
    “3σ Variance” or “Kalman Filter” is applied only when Step1 does not filter outliers enough.
2.1 RO Permeate Water Quality Prediction > Introduction
Feed Flow Rate Raw Data (1minute span)
(1)
(2)
DATE
DATE
DATE
y=0
More than 10 min
Changing rate
More than 20%
Y
Y
Y
(3)
Constant value lasts long term
Changing Rate is high
Value is 0
Local Rules in Step1

## Slide 10: Sequential Prediction (1 week Training and 1 week Prediction)
2.1 RO Permeate Water Quality Prediction > Introduction
・・・
We
e
k 55
We
e
k 56
We
e
k 2
We
e
k 3
We
e
k４
・・・
We
e
k 56
We
e
k 3
We
e
k 4
We
e
k 2
We
e
k 3
We
e
k 1
We
e
k 2
Training
Prediction trend
predict
Training
Training
Training
predict
predict
predict
“Prediction trend” is totally compiled with each weekly prediction trend all through the period.

## Slide 11: Today’s Topic Agenda
Multiple Regression Model
    A-1：Prediction results from systematically pre-processed data
        Target① / Target④
    A-2：Difference in prediction results with and without preprocessing
Radom Forest（New Approach）
    B-1：Prediction results from systematically pre-processed data with Radom Forest Model
        Target① / Target④
    B-2：Difference in prediction results between Multiple Regression Model（A-1） and Radom Forest Model（B-1）
    B-3：Consideration of B-2 （Characteristics of Random Forest）
Extra Trial（variation of A-1 and B-1：systematically pre-processing with minor manual tuning）
  A-1-α：Prediction results from systematically pre-processing with minor manual tuning
  B-1-α：Prediction results from systematically pre-processing with minor manual tuning
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results

## Slide 12: Today’s Topic Agenda
Multiple Regression Model
    A-1：Prediction results from systematically pre-processed data
        Target① / Target④
    A-2：Difference in prediction results with and without preprocessing
Radom Forest（New Approach）
    B-1：Prediction results from systematically pre-processed data with Radom Forest Model
        Target① / Target④
    B-2：Difference in prediction results between Multiple Regression Model（A-1） and Random Forest（B-1）
    B-3：Consideration of B-2 （Characteristics of Random Forest）
Extra Trial（variation of A-1 and B-1：systematically pre-processing with minor manual tuning）
    A-1-α：Prediction results from systematically pre-processing with minor manual tuning
    B-1-α：Prediction results from systematically pre-processing with minor manual tuning
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by MLR
・・・P13~16

## Slide 13
Index | Stage1 Permeate EC
RMSE | 1.88 (uS/cm)
MAPE | 5.24 (%)
Pre-processed actual data
Predicted data
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by MLR
Prediction results by Multiple Linear Regression
Stage1 Permeate EC [uS/cm]

## Slide 14
Index | Combined Permeate TOC
RMSE | 0.023* (mg/L)
MAPE | 18.46* (%)
Pre-processed actual data
Predicted data
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by MLR
Prediction results by Multiple Linear Regression
Combined Permeate TOC [mg/L]

## Slide 15
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by MLR
Impact of Preprocessing on Prediction
preprocessing
Stage1 Permeate EC [uS/cm]
Difference in prediction results with and without preprocessing.

## Slide 16
Feed Pressure
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by MLR
Impact of Data Disturbance on Prediction
①
②
③
⑤
①
②
③
⑤
Target ① Stage1 Permeate EC
④
④

## Slide 17: Today’s Topic Agenda
Multiple Regression Model
    A-1：Prediction results from systematically pre-processed data
        Target① / Target④
    A-2：Difference in prediction results with and without preprocessing
Radom Forest（New Approach）
    B-1：Prediction results from systematically pre-processed data with Random Forest
        Target① / Target④
    B-2：Difference in prediction results between Multiple Regression Model（A-1） and Random Forest（B-1）
    B-3：Consideration of B-2 （Characteristics of Random Forest）
Extra Trial（variation of A-1 and B-1：systematically pre-processing with minor manual tuning）
  A-1-α：Prediction results from systematically pre-processing with minor manual tuning
  B-1-α：Prediction results from systematically pre-processing with minor manual tuning
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by Random Forest

## Slide 18
Index | Stage1 Permeate EC
RMSE | 0.88 (uS/cm)
MAPE | 3.20 (%)
Pre-processed actual data
Predicted data
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by Random Forest
Prediction results by Random Forest
Stage1 Permeate EC [uS/cm]

## Slide 19
Index | Combined Permeate TOC
RMSE | 0.017 (mg/L)
MAPE | 15.02 (%)
Pre-processed actual data
Predicted data
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results by Random Forest
Prediction results by Random Forest
Combined Permeate TOC [mg/L]

## Slide 20
Radom Forest
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results
①
②
③
④
⑤
①
②
③
④
⑤
Multiple Regression Model
Stage1 Permeate EC [uS/cm]
Comparing MLR and Random Forest

## Slide 21
x
y
Radom Forest Model
Linear Model
Region1 and Region2 included 3 elements.
The region is divided by the threshold of x = 10.
Inside the region y has constant value.
Ex.
→independent of y value of ★, predicted y value is
in the Region2.
2.2 RO Permeate Water Quality Prediction > Prediction and Preprocessing Results
Consideration: Characteristics of Random Forest
Example: different impact of outlier depending on Models
The predicted y value depends on x value of ★.
→The predicted y value is y3 in the proportion of x value of ★.
Random forest Model is more stable to outliers
x
★
★
Outlier
★
Learned model
Outlier
★
Learned model
y
10
Region１
Region2

## Slide 22
2.2 RO Permeate Water Quality Prediction > Minor Manual Preprocessing
Changing Pretreatment Parameters for Permeate TOC
Before
After
Minor manual tuning is effective to minimize the error value. But tuning performance is highly influence of artifact.
Multiple Regression Model
Radom Forest
minor manual tuning
minor manual tuning
A-1
A-1-α
B-1-α
B-1
Combined Permeate TOC [mg/L]

## Slide 23: Agenda
RO Operation Optimization
RO Permeate Water Quality Prediction / Q&A
RO Optimization Simulation / Q&A
RO Membrane Scaling Modeling / Q&A
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 24: Summary
Develop the RO optimization simulator with new optimizer built in, not based on DDMO.
  It assumes that Yokogawa engineer can use it although it has not yet been fully tested.
  It needs more functions for pilot/demo-scale implementation.
Estimate the optimization effect comparing operational cost.
3. RO Optimization Simulation

## Slide 25: Functional Configuration of RO Optimization Simulator
3. RO Optimization Simulation > Simulator
Unify the file format, e.g., add calculated tag and up/down resampling according to given timespan based on master data without outliers.
Generate optimization / prediction model files with user-specified modeling and parameter files using data in the training / optimization period.
Calculate prediction model error by input optimization variables fixed to actual value into optimization model, i.e., predict validation.
Solve the RO plant scheduling problem by optimizer.
Calculate each average value and LRV of water quality, and draw each variable trend chart including LRV.
Pre-processing
Generate Model and Params
Model Validation
Optimize
Post-processing

## Slide 26: Module Configuration
3. RO Optimization Simulation > Simulator
main.py
Optimization Module
Optimization Problem
model
Input data
Definition objective and constraint functions.py
import_model.py
1st permeate EC Prediction module
Defined Optimization Problem
Defined Optimization Solver
Automatically created model files by training
pkg
config.ini
2nd permeate EC Prediction module
Execute each function

## Slide 27: Flow Chart for RO Optimization
3. RO Optimization Simulation > Problem Formulation
We define the flow chart, variables, mathematical models.
  The model dose not yet include RO Membrane Scaling / Fouling model.
RO Whole Part
RO Each Stage Part
Exogenous Variable
Predictive Variable
(water quality)
Mathematical Model
(prediction model)
Notes: This is the flow chart for Las Virgenes model. I divided into the RO whole part and RO each stage part. The storage object is exogenous variable and the square object is predictive variable that is water quality. The hexagon object is mathematical model and have both input and output variable. The arrow toward the object is input variable and the arrow from the object is output variable. Especially, the four objects enclosed in the square are the prediction model constructed by Imoto-san.

## Slide 28: Optimization Problem
3. RO Optimization Simulation > Problem Formulation
Objective Function
Main Constraint Conditions
Water Quality Standards and Upper / Lower limit
Logarithmic Reduction Value (LRV):
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Combined EC LRV | - | 1.5 | 2.0
Combined TOC LRV | - | 1.5 | 2.2
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Combined EC LRV | - | 1.5 | 2.0
Combined TOC LRV | - | 1.5 | 2.2
are calculated by the prediction model at the previous part.
UF Filtrate Total Chlorine
Minimizing chemical cost while satisfying water quality standards.
Total Steps
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 29: Optimization Algorithm
3. RO Optimization Simulation > Optimizer
We must select the optimization algorithm the problem class.
  This problem class can be nonlinear or black-box continuous optimization in future efforts of modeling.
Therefore, we use the combined algorithm with some known metaheuristic algorithms.
  I wrote the python code from scratch and introduced into the optimization simulator.
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 30: Metaheuristic Algorithm
3. RO Optimization Simulation > Optimizer
We use the combined algorithm with SHADE and the feasibility rule.
  SHADE[1] is the state-of the art solver in the black-box optimization field.
  Metaheuristic algorithm + CHT considers both of the objective function value and the constraint violation .
Unconstrained Prob.
Constrained Prob.
SHADE, GA etc.
Metaheuristics Algorithm
Constraint Handling Techniques (CHTs)
None
SHADE, GA etc.
Feasibility Rule, Static Penalty etc.
+
Constraints:
Amount of Constraint Violation:
[1] R. Tanabe et al.: “Success-History Based Parameter Adaptation for Differential Evolution” (2013)
Notes: Optimization solver for unconstrained nonlinear and Black-box optimization classes as well as Genetic Algorithm.

## Slide 31: Constraint Handling Techniques
3. RO Optimization Simulation > Optimizer
CHT is divided into 3 classes[2].
Feasibility Rule,
Death Penalty,
Two-Phase Framework
Adaptive Penalty
Adaptive MOEA/D
CM
MCR
Penalty-based CHT
Separatist-based CHT
Multi-objective-based CHT
Decomposition
Pareto Ranking
Ranking
Switching
Method
Evaluate
Evaluate separated
Evaluate both
Example
Search Efficiency of Trade-off Region
Low
Middle
High
Computational Complexity
Low
Low
High
[2] W. Kumagai and K. Yasuda: “Black-Box Optimization and Its Applications,” Innovative Systems Approach for Facilitating Smarter World, Springer Nature Singapore (2023)
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 32: Concept of Feasibility Rule
3. RO Optimization Simulation > Optimizer
Select a solution putting before .
Selection pressure for the feasible region is STRONG.
Population
# | Compared | Select
1. | Violated solutions | Lower
2. | Feasible and violated solutions | Feasible solution
3. | Feasible solutions | Lower
# | Compared | Select
1. | Violated solutions | 
2. | Feasible and violated solutions | Feasible solution
3. | Feasible solutions | 
1st Step
If two solutions are compared, use the following rule:
2nd Step
Objective Function Value
Constraint Violation
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 33: Permeate Water Quality
The prediction performance for global trends is good.
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
3. RO Optimization Simulation > Prediction Result
Blue: Actual / Orange: Prediction
Actual Ave.: 0.067 [mg/L],
Predict Ave.: 0.064 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Predict Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Predict Ave.: 2.03
Actual Ave.: 1.83,
Predict Ave.: 1.83
Training Period: from March 7th to 14th, 2022 (1week)
Optimization Period : from March 14th to 21th, 2022 (1week)
1hour interval data
*The results are NOT optimized when input data is fixed to actual data.

## Slide 34: Search Solution Transition (during Generations)
After getting a feasible solution, the solution is improving .
3. RO Optimization Simulation > Optimization Results
*Total calculation time is about 10 minutes.
(Generations)
Objective Function Value
Constraint Violation
Get feasible solution
Best Solution Transition
Population size: 100

## Slide 35: Chemical and Exogeneous Variables
UF Total Chlorine [mg/L] (Chemical Dosing Cost)
S1 Feed Pressure [psi] (Fixed)
S1 Feed Flow [gpm] (Fixed)
S1 Feed EC [uS/cm] (Fixed)
Feed TOC [mg/L] (Fixed)
3. RO Optimization Simulation > Optimization Results
The schedule shows reducing chemical costs comparing to actual data.
Blue: Actual / Orange: Optimized
Actual Ave.: 0.40 [mg/L],
Optimized Ave.: 0.38 [mg/L]

## Slide 36: Water Quality Variable
Actual Ave.: 0.067 [mg/L],
Optimized Ave.: 0.063 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Optimized Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Optimized Ave.: 2.03
Actual Ave.: 1.83,
Optimized Ave.: 1.83
There is a little change but meeting the WQ standards of LRV.
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
3. RO Optimization Simulation > Optimization Results

## Slide 37: Optimization Effect Calculation
There is a little improvement in the period and condition.
  This model does NOT yet RO membrane fouling model.
3. RO Optimization Simulation > Optimization Effect
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err.
Total Chlorine [mg/L] | 0.40 | 0.38 | - 0.02 |  | - 0.02
EC [uS/cm] | 20.76 | 20.87 | + 0.11 | + 0.11 | - 0.0004
TOC [mg/L] | 0.067 | 0.063 | - 0.004 | - 0.004 | + 0.0004
LRV EC | 1.83 | 1.82 | - 0.01 | - 0.01 | + 0.002
LRV TOC | 2.01 | 2.03 | + 0.02 | + 0.02 | + 0.003

## Slide 38: Future Tasks
To introduce Random Forest into optimization.
  Metaheuristic algorithm calls RF 500,000 times, so many calculation time.
To introduce RO membrane Fouling model and determine chemical cost considering RO Fouling.
3. RO Optimization Simulation > Optimization Effect

## Slide 39: Overview of Scaling Estimation
Overview of Scaling Estimation
Concentration Polarization
Saturation Index
Chemical Dosage
[1] https://onl.bz/f1JewkV
[1],[2]
[4]Effect of residence time on the degree of CaCO3
precipitation in the presence of an anti-scalant
[2] famous textbook
[3]
[3]https://wwwbrr.cr.usgs.gov/projects/GWC_chemtherm/pubs/wq4fdoc.pdf
4. RO Membrane Scaling Modeling

## Slide 40: Calculation Methods : Concentration Polarization
Step1 : Calc parameter from data sheet
  mass transfer coefficient
Step2 : Calc brine EC and at each stage
Step3 : Calc form , and
means unit transformation coefficient
” denotes RO stage number, locations (feed, membrane surface, permeate, brine)
4. RO Membrane Scaling Modeling

## Slide 41: Calculation Methods : Concentration Polarization
Step4 : Calc concentration on membrane surface
4. RO Membrane Scaling Modeling

## Slide 42: Calculation Methods : Saturation Index
What is Saturation Index?
4. RO Membrane Scaling Modeling

## Slide 43: Calculation Methods : Saturation Index
USGS software
  software can calculate SI depends on following equations
[3]https://wwwbrr.cr.usgs.gov/projects/GWC
_chemtherm/pubs/wq4fdoc.pdf
…
…
…
4. RO Membrane Scaling Modeling

## Slide 44: Calculation Methods : Saturation Index
Si concentration vs. SI
  Problem settings
    All parameters without Si concentration are fixed
    Changing Si concentration from 0 to 450[mg/L]
Relationship between Anti-Scalant and Concentration
  Focus on 3rd stage polarization
Need Anti-Scalant
4. RO Membrane Scaling Modeling

## Slide 45: Q&A / Discussion
4. RO Membrane Scaling Modeling

## Slide 47: [LVMWD] RO System Configuration and Measurement Points
P
・Feed Free Chlorine
・Feed Conductivity
・Feed pH, TOC, Temp
・Feed Pressure
・Feed Flow (Calc)
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Combined Permeate TOC
・Combined Permeate Conductivity
・Concentrate Pressure
・Concentrate Flow
・Inlet Free Chlorine
・Inlet Total Chlorine
・Inlet pH
・Inlet UVT
・Inlet Flow
UV
・Outlet Free Chlorine
・Outlet Total Chlorine
・Inlet UVT
・UV Dose
・UV Intensity
・UV Lamp Power (Constant 50%)
RO 1st Stage
RO 2nd Stage
RO 3rd Stage
Feed Pressure
Concentrate Pressure
Feed Pressure
P
This pump decides the feed flow to RO.
a
b
c
d
e
<Differential Pressure>
Stage 1 = －
Stage 2 = －
Stage 3 = －
a
b
b
c
d
e

## Slide 48: Data Preprocessing
  Step1 : Data Cleaning Getting rid of the data during the period when it is as following: ① First Feed Flow Rate equal 0, ② The measurement value remains same value for more than 10 mints, ③ Changing rate of measurement value is more than 20% ( / mint) and etc.
2. RO Permeate Water Quality Prediction
Feed Flow Rate Raw Data
Zoom up
①
②
③
  Step2 : Filtering This step (ⅰ or ⅱ) is applied only when step1 pretreatment does not have enough efficacy.
    Analysis of Variance（Removing the outlier which is beyond 3σ.）
    Kalman Filter is applied.
DATE
DATE
DATE
y=0
More than 10 min
Changing rate
More than 20%
Y
Y
Y

## Slide 49: Overview of the water quality prediction model
2. RO Permeate Water Quality Prediction
RO system
measuring point
P
pump
Target①
Target②
Target③
Target④
RO Permeate Water Quality Prediction targets are Target①~④
  Focused Period: July 1st, 2021 ~ July 27th, 2022
    all variables are available and operational situation with RO membrane is stable.
  Target Variables: 1st to 3rd stage permeate conductivity and combined TOC
    Treated water is required to satisfy the standard indicated permeate conductivity and TOC.

## Slide 50
Index | Stage2 Permeate EC
RMSE | 2.46* (uS/cm)
MAPE | 5.59* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ② Stage2 Permeate EC ～

## Slide 51
Index | Stage3 Permeate EC
RMSE | 2.30* (uS/cm)
MAPE | 4.70* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ③ Stage3 Permeate EC ～

## Slide 52
Index | Stage2 Permeate EC
RMSE | 1.40* (uS/cm)
MAPE | 4.37* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ② Stage2 Permeate EC ～

## Slide 53
Index | Stage3 Permeate EC
RMSE | 2.02 (uS/cm)
MAPE | 4.06 (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ③ Stage3 Permeate EC ～

## Slide 54: Variable List
LVMWD
ID No. | Description | Units | Opt. Variable / Fixed Parameter
ID0000 | UF Filtrate Total Chlorine | ton/day | Optimization Variable
ID0001 | Feed EC |  | Fixed Parameter
ID0002 | Feed TOC | mg/L | Fixed Parameter
ID0003 | Feed Temperature |  | Fixed Parameter
ID0004 | Feed pH | - | Fixed Parameter
ID0100 | Stage 1 Feed Pressure | psi | Fixed Parameter
ID0101 | Stage 1 Feed Flow Rate | gpm | Fixed Parameter
ID0102 | Stage 1 Permeate Flow Rate | gpm | Fixed Parameter
ID0200 | Stage 2 Feed Flow Rate | gpm | Fixed Parameter
ID0201 | Stage 2 Permeate Flow Rate | gpm | Fixed Parameter
ID0300 | Stage 3 Feed Pressure | psi | Fixed Parameter
ID0301 | Stage 3 Feed Flow Rate | gpm | Fixed Parameter
ID1000 | Stage 1 Permeate EC |  | Intermediate Variable
ID2000 | Stage 2 Feed EC |  | Intermediate Variable
ID2001 | Stage 2 Permeate EC |  | Intermediate Variable
ID3000 | Stage 3 Feed EC |  | Intermediate Variable
ID3001 | Stage 3 Permeate EC |  | Intermediate Variable
ID4000 | Permeate EC |  | Intermediate Variable
ID4001 | Permeate TOC | mg/L | Intermediate Variable
ID No. | Description | Units | Opt. Variable / Fixed Parameter
ID0000 | UF Filtrate Total Chlorine | ton/day | Optimization Variable
ID0001 | Feed EC |  | Fixed Parameter
ID0002 | Feed TOC | mg/L | Fixed Parameter
ID0003 | Feed Temperature |  | Fixed Parameter
ID0004 | Feed pH | - | Fixed Parameter
ID0100 | Stage 1 Feed Pressure | psi | Fixed Parameter
ID0101 | Stage 1 Feed Flow Rate | gpm | Fixed Parameter
ID0102 | Stage 1 Permeate Flow Rate | gpm | Fixed Parameter
ID0200 | Stage 2 Feed Flow Rate | gpm | Fixed Parameter
ID0201 | Stage 2 Permeate Flow Rate | gpm | Fixed Parameter
ID0300 | Stage 3 Feed Pressure | psi | Fixed Parameter
ID0301 | Stage 3 Feed Flow Rate | gpm | Fixed Parameter
ID1000 | Stage 1 Permeate EC |  | Intermediate Variable
ID2000 | Stage 2 Feed EC |  | Intermediate Variable
ID2001 | Stage 2 Permeate EC |  | Intermediate Variable
ID3000 | Stage 3 Feed EC |  | Intermediate Variable
ID3001 | Stage 3 Permeate EC |  | Intermediate Variable
ID4000 | Permeate EC |  | Intermediate Variable
ID4001 | Permeate TOC | mg/L | Intermediate Variable

## Slide 55: 透過水質
トレンドを大まかに捉えているが、ECの予測値が実績よりも若干低い。
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
2.2 OCWD > 1st week 予測結果
Blue: Actual / Orange: Prediction
Actual Ave.: 0.055 [ppm],
Predict Ave.: 0.052 [ppm]
Actual Ave.: 23.48 [uS/cm],
Predict Ave.: 18.61 [uS/cm]
Actual Ave.: 2.22,
Predict Ave.: 2.24
Actual Ave.: 1.88,
Predict Ave.: 1.99

## Slide 56: 探索結果（最良解の推移）
実行可能解を得て、コストを改善する解が得られている。
2.2 OCWD > 1st week 最適化結果
10,000の半分で止めた
Blue: Objective Function Value /
Orange: Constraint Violation
約9分

## Slide 57: 操作計画：コスト変数と固定変数
Sulfuric Acid [ton/hour]（コスト）
S1流入圧力 [psi]（固定）
S1流入量 [gpm]（固定）
S1流入EC [uS/cm]（固定）
流入TOC [ppm]（固定）
Inhibitor [ton/hour] （コスト）
2.2 OCWD > 1st week 最適化結果
LRV基準の制約によって、Inhibitorが実績とほぼ同じ値になっている。
Blue: Actual / Orange: Optimized
Actual Ave.: 0.39 [ton/hour],
Optimized Ave.: 0.38 [ton/hour]
Actual Ave.: 0.0559 [ton/hour],
Optimized Ave.: 0.0560 [ton/hour]

## Slide 58: 操作計画：透過水質
ECのLRV基準の上限に位置する解となっている。
2.2 OCWD > 1st week 最適化結果
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
Actual Ave.: 0.055 [ppm],
Optimized Ave.: 0.053 [ppm]
Actual Ave.: 23.5 [uS/cm],
Optimized Ave.: 18.7 [uS/cm]
Actual Ave.: 2.22,
Optimized Ave.: 2.23
Actual Ave.: 1.88,
Optimized Ave.: 1.98

## Slide 59: コスト換算
約47$/day(18K$/year, 2.5M\/year)の削減効果と見積もれる。
  ただし、この条件では、ほぼ改善の余地が無いと見積もれる。
2.2 OCWD > 1st week 最適化結果
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err. | Cost [$/day]
Acid [ton/hour] | 0.39 | 0.38 | - 0.009 |  | - 0.009 | - 53.3
Inhibitor [ton/hour] | 0.0559 | 0.0560 | + 0.0001 |  | + 0.0001 | + 6.22
EC [uS/cm] | 23.5 | 18.7 | - 4.74 | - 4.87 | + 0.13 | 
TOC [mg/L] | 0.055 | 0.053 | - 0.002 | - 0.003 | + 0.001 | 
LRV EC | 1.88 | 1.98 | + 0.30 | - 0.01 | - 0.003 | 
LRV TOC | 2.217 | 2.234 | + 0.02 | + 0.02 | - 0.005 | 
Total |  |  |  |  |  | - 47.1