## Slide 1: NAWI RO Analysis Progress Report
W. Kumagai, H. Soya, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
August 30th, 2023
SGDC

## Slide 2: Agenda
RO Operation Optimization
RO Permeate Water Quality Prediction
RO Optimization Simulation
RO Membrane Scaling Modeling
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 3: Objective of RO Optimization
Chemical dosing costs are minimized considering RO membrane condition within the range of maintaining water quality and flow rate.
  Maintaining high recovery rate, good water quality (high salt rejection), and extending RO membrane life.
  Considering water quality, permeate flow rate, and RO clogging status.
RO
NaClO
UF
Sulfuric Acid／Anti-Scalant
Potable Water
UV / AOP
UV Radiation with H2O2 or NaClO
Water quality
Degree of Clogging
Membrane cleaning
Membrane life
1. RO Operation Optimization
Given Region
Given Region
Subject to be optimization target if interchangeable with RO.
Chemical costs
Chemical costs
Water quality and flow rate to be maintained
Clogging due to fouling Scaling by crystallization Bio-fouling by deposit
Notes: First, I explain RO data analysis and optimization policy. This shows potable water reuse process. Water from sewage plant is treated by this process and supplied to potable reuse.
It mainly consists of UF, RO, UV, and AOP process units. The objective of RO optimization shows operating costs are ~. There are important costs in many places, for example, chemical cost, RO membrane cleaning cost, and electricity cost. Moreover there are considering conditions in many places, for example, recover rate, water quality, and RO membrane life. So, optimization strategy is to select critical costs and conditions according to priority.
Based on the stages, RO analytical policy is to expand the control and considered value step by step. First stage is to control and consider yellow values. Green values are added in second stage and red values are added in third stage as well. But, gray regions are considered as given area in RO optimization, so they are fixed to actual value when calculation.

## Slide 4
3 Stages configuration.
RO permeate TOC and Conductivity are water quality data.
  Monitoring LRV (logarithmic reduce value) as water-quality standards.
1. RO Operation Optimization
Overall view of LVMWD RO system
RO system
measuring point
P
pump
Water Quality Targets are shown in red.

## Slide 5: Plant Scheduling Optimization
RO optimization problem is formulated into a scheduling optimization.
The procedure consists of the following steps.
1. RO Operation Optimization
A
B
C
Facility Model
: Optimization Variable
1. Drawing Flow Chart
(Operational Cost)
(Facility Characteristics)
2. Formulation
Optimization Problem
Time
Operational Cost is $XX.
3. Calculation
Operational Schedule
Sample Flow Chart
Notes: RO optimization problem is formulated into a plant scheduling optimization. The procedure~. First step is drawing flow chart. In this chart, arrows connecting objects are assigned optimization variables. The object plays the role of exogenous variable, mathematical model, and predictive variable. Second step is formulation optimization problem. I define the minimizing the objective function and the constraints. Third step is calculation operational schedule. I solve the formulated problem using optimization algorithm.

## Slide 6: Desktop Evaluation Flow Chart
1. RO Operation Optimization
Calculate the optimization effect
Plant Info. Check
Step1
Model Construction
Step2
Step3
Optimization
Effect Calculation
Check the plant flow & data
Step4
Construct and validate the plant model
Execute optimization simulation
Check the plant flow chart, control & manipulated variable, evaluation index, and data trends.
Decide optimization story and modeling way.
Construct the plant model including water quality prediction models.
Especially prediction models are validated individually.
Implement the optimization problem and optimizer.
Execute simulation and validate/check the behavior.
Compare optimization results with operation actual data in the past.
Detailed in Section 2
Detailed in Section 3
Notes: We have taken the following chart.

## Slide 7: Agenda
Multiple Regression Model
    A-1：Prediction results from systematically pre-processed data
        Target① / Target② / Target③ / Target④
    A-2：Difference in prediction results with and without preprocessing
Radom Forest（New Approach）
    B-1：Prediction results from systematically pre-processed data with Random Forest
        Target① / Target② / Target③ / Target④
    B-2：Difference in prediction results between Multiple Regression Model（A-1） and Random Forest（B-1）
    B-3：Consideration of B-2 （Characteristics of Random Forest）
Extra Trial（variation of A-1 and B-1：systematically pre-processing with minor manual tuning）
    A-1-α：Prediction results from systematically pre-processing with minor manual tuning
    B-1-α：Prediction results from systematically pre-processing with minor manual tuning
2. RO Permeate Water Quality Prediction

## Slide 8: Data Preprocessing
2. RO Permeate Water Quality Prediction

## Slide 9: Sequential Prediction
2. RO Permeate Water Quality Prediction

## Slide 10
Index | Stage1 Permeate EC
RMSE | 1.88 (uS/cm)
MAPE | 5.24 (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ① Stage1 Permeate EC ～

## Slide 11
Index | Combined Permeate TOC
RMSE | 0.023* (mg/L)
MAPE | 18.46* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ④ Combined Permeate TOC ～

## Slide 12
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-2：Difference in prediction results with and without preprocessing
preprocessing
～ Target ① Stage1 Permeate EC ～

## Slide 13
Feed Pressure
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-2：Difference in prediction results with and without preprocessing
～ Data turbulence disturb the prediction ～
①
②
③
⑤
①
②
③
⑤
Target ① Stage1 Permeate EC
④
④

## Slide 14
Index | Stage1 Permeate EC
RMSE | 0.88 (uS/cm)
MAPE | 3.20 (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ① Stage1 Permeate EC ～

## Slide 15
Index | Stage4 Permeate EC
RMSE | 0.017 (mg/L)
MAPE | 15.02 (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ④ Stage4 Permeate EC ～

## Slide 16
Radom Forest
2. RO Permeate Water Quality Prediction
～ Target ① Stage1 Permeate EC ～
B-2：Difference in prediction results between Multiple Regression Model（A-1） and Random Forest（B-1）
①
②
③
④
⑤
①
②
③
④
⑤
Multiple Regression Model

## Slide 17
x
y
Radom Forest Model
Linear Model
Region1 and Region2 included 3 elements.
The region is divided by the threshold of x = 10.
Inside the region y has constant value.
Ex.
→independent of y value of ★, predicted y value is
in the Region2.
2. RO Permeate Water Quality Prediction
B-3：Consideration of B-2 （Characteristics of Random Forest）
Example：different impact of outlier depending on Models
The predicted y value depends on x value of ★.
→The predicted y value is y3 in the proportion of x value of ★.
Random forest Model is more stable to outliers
x
★
★
Outlier
★
Learned model
Outlier
★
Learned model
y
10
Region１
Region2

## Slide 18
2. RO Permeate Water Quality Prediction
Result： Changing Pretreatment Parameters for Permeate TOC
Before
After
Minor manual tuning is effective to minimize the error value. But tuning performance is highly influence of artifact.
Multiple Regression Model
Radom Forest
minor manual tuning
minor manual tuning
A-1
A-1-α
B-1-α
B-1
～ Target④： Permeate TOC ～

## Slide 19: Summary
Develop the RO optimization simulator with new optimizer built in, not based on DDMO.
  It assumes that Yokogawa engineer can use it although it has not yet been fully tested.
  It needs more functions for pilot/demo-scale implementation.
Estimate the optimization effect comparing operational cost.
3. RO Optimization Simulation

## Slide 20: Functional Configuration of RO Optimization Simulator
3. RO Optimization Simulation > Simulator
Unify the file format, e.g., add calculated tag and up/down resampling according to given timespan based on master data without outliers.
Generate optimization / prediction model files with user-specified modeling and parameter files using data in the training / optimization period.
Calculate prediction model error by input optimization variables fixed to actual value into optimization model, i.e., predict validation.
Solve the RO plant scheduling problem by optimizer.
Calculate each average value and LRV of water quality, and draw each variable trend chart including LRV.
Pre-processing
Generate Model and Params
Model Validation
Optimize
Post-processing

## Slide 21: Module Configuration
3. RO Optimization Simulation > Simulator
pkg
main.py
Optimization Module
Optimization Problem
model
params
Definition objective and constraint functions
import_model.py
Water quality Prediction module
Optimization Problem Definition
Optimization Solver Definition
unit_algorithm.py
algorithms
Definition objective and constraint functions
import given model files from outside

## Slide 22: Flow Chart for RO Optimization
3. RO Optimization Simulation > Problem Formulation
We define the flow chart, variables, mathematical models.
RO Whole Part
RO Each Stage Part
Exogenous Variable
Predictive Variable
(water quality)
Mathematical Model
(prediction model)
Notes: This is the flow chart for Las Virgenes model. I divided into the RO whole part and RO each stage part. The storage object is exogenous variable and the square object is predictive variable that is water quality. The hexagon object is mathematical model and have both input and output variable. The arrow toward the object is input variable and the arrow from the object is output variable. Especially, the four objects enclosed in the square are the prediction model constructed by Imoto-san.

## Slide 23: Optimization Problem
3. RO Optimization Simulation > Problem Formulation
Objective Function
Main Constraint Conditions
Water Quality Standards and Upper / Lower limit
Logarithmic Reduction Value (LRV):
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Stage 1 EC LRV | - | 1 | 2.5
Stage 2 EC LRV | - | 1 | 2.5
Stage 3 EC LRV | - | 1 | 2.5
TOC LRV | - | 1 | 2.0
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Permeate TOC |  | 0 | 0.15
Stage 1 EC LRV | - | 1 | 2.5
Stage 2 EC LRV | - | 1 | 2.5
Stage 3 EC LRV | - | 1 | 2.5
TOC LRV | - | 1 | 2.0
are calculated by the prediction model at the previous part.
UF Filtrate Total Chlorine
Minimizing chemical cost while satisfying water quality standards.
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 24: Optimization Algorithm
3. RO Optimization Simulation > Optimizer
-.
  I write the python code from scratch.
We must select the optimization algorithm the problem class.
  This problem class can be nonlinear or black-box optimization in future efforts of modeling.
Therefore, we will use the combined algorithm with SHADE and the feasibility rule.
  They are classified as metaheuristic algorithm as well as Genetic Algorithm.
  SHADE is the state-of-the-art solver in the black-box optimization field.
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 25: Constraint Handling Techniques
3. RO Optimization Simulation > Optimizer
のトレードオフ領域の探索は多目的最適化ベースが有利。
Feasibility Rule、
Death Penalty、
Two-Phase Framework
Adaptive Penalty
Adaptive MOEA/D
CM
MCR
ペナルティベース
分離ベース
多目的最適化ベース
問題分割
パレートランキング
ランキング
切替
方法
で評価
とを分離して評価
の二目的最適化
例
トレードオフ領域の探索効率
低
中
高
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 26: Constraint Handling Techniques
3. RO Optimization Simulation > Optimizer
多目的アプローチ以外に、制約違反量削減優先も採用した。
  仮説：可能領域への収束の観点では、違反量削減で優秀な近傍生成を使うほうが有利
よりもを優先して、解を選択する方法
基本的に可能領域への選択圧が強い
Feasibility Rule
項目 | Adaptive MOEA/D | 適応型PSO／適応型DE
解の評価・選択 | 多目的最適化（問題分割） | Feasibility Rule
近傍生成 | 実数値GA | Activity Feedback PSO／JADE／SHADE
違反解同士の比較
可能解と違反解の比較
可能解同士の比較
⇒ で比較・選択
⇒ 可能解を選択
⇒ で比較・選択
MOEA/D
個体に異なる重みを与えて、部分問題に分割する方法
のパレートフロンティアへの選択圧が強い
探索点
探索点
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, RO process operators monitor the logarithmic reduction value called LRV as standards. The LRV’s upper of EC is 2.5 and LRV’s upper of TOC is 2.0 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 27: Permeate Water Quality
The prediction performance for global trends is good.
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
3. RO Optimization Simulation > Prediction Result
Blue: Actual / Orange: Prediction
Actual Ave.: 0.067 [mg/L],
Predict Ave.: 0.064 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Predict Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Predict Ave.: 2.03
Actual Ave.: 1.83,
Predict Ave.: 1.83
Training Period: from March 7th to 14th, 2022 (1week)
Optimization Period : from March 14th to 21th, 2022 (1week)
1hour interval data
*The results are NOT optimized when input data is fixed to actual data.

## Slide 28: Search Solution Transition (during Generations)
After getting a feasible solution, the solution is improving.
3. RO Optimization Simulation > Optimization Results
Blue: Objective Function Value /
Orange: Constraint Violation
*Total calculation time is about 10 minutes.
(Generations)

## Slide 29: Chemical and Exogeneous Variables
UF Total Chlorine [mg/L]（コスト）
S1流入圧力 [psi]（固定）
S1流入量 [gpm]（固定）
S1流入EC [uS/cm]（固定）
流入TOC [mg/L]（固定）
3. RO Optimization Simulation > Optimization Results
The schedule shows reducing chemical costs comparing to actual data.
Blue: Actual / Orange: Optimized
Actual Ave.: 0.40 [mg/L],
Optimized Ave.: 0.38 [mg/L]

## Slide 30: Water Quality Variable
Actual Ave.: 0.067 [mg/L],
Optimized Ave.: 0.063 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Optimized Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Optimized Ave.: 2.03
Actual Ave.: 1.83,
Optimized Ave.: 1.83
There is a little change but meeting the WQ standards of LRV.
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
3. RO Optimization Simulation > Optimization Results

## Slide 31: Optimization Effect Calculation
There is a little improvement in the period and condition.
3. RO Optimization Simulation > Optimization Effect
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err.
Total Chlorine [mg/L] | 0.40 | 0.38 | - 0.02 |  | - 0.02
EC [uS/cm] | 20.76 | 20.87 | + 0.11 | + 0.11 | - 0.0004
TOC [mg/L] | 0.067 | 0.063 | - 0.004 | - 0.004 | + 0.0004
LRV EC | 1.83 | 1.82 | - 0.01 | - 0.01 | + 0.002
LRV TOC | 2.01 | 2.03 | + 0.02 | + 0.02 | + 0.003

## Slide 32: Overview of Scaling Estimation
Overview of Scaling Estimation
Concentration Polarization
Saturation Index
Chemical Dosage
[1] https://onl.bz/f1JewkV
[1],[2]
[4]Effect of residence time on the degree of CaCO3
precipitation in the presence of an anti-scalant
[2] famous textbook
[3]
[3]https://wwwbrr.cr.usgs.gov/projects/GWC_chemtherm/pubs/wq4fdoc.pdf
4. RO Membrane Scaling Modeling

## Slide 33: Calculation Methods : Concentration Polarization
Step1 : Calc parameter from data sheet
  mass transfer coefficient
Step2 : Calc brine EC and at each stage
Step3 : Calc form , and
means unit transformation coefficient
” denotes RO stage number, locations (feed, membrane surface, permeate, brine)
4. RO Membrane Scaling Modeling

## Slide 34: Calculation Methods : Concentration Polarization
Step4 : Calc concentration on membrane surface
4. RO Membrane Scaling Modeling

## Slide 35: Calculation Methods : Saturation Index
What is Saturation Index?
4. RO Membrane Scaling Modeling

## Slide 36: Calculation Methods : Saturation Index
USGS software
  software can calculate SI depends on following equations
[3]https://wwwbrr.cr.usgs.gov/projects/GWC
_chemtherm/pubs/wq4fdoc.pdf
…
…
…
4. RO Membrane Scaling Modeling

## Slide 37: Calculation Methods : Saturation Index
Si concentration vs. SI
  Problem settings
    All parameters without Si concentration are fixed
    Changing Si concentration from 0 to 450[mg/L]
Relationship between Anti-Scalant and Concentration
  Focus on 3rd stage polarization
Need Anti-Scalant
4. RO Membrane Scaling Modeling

## Slide 38: Question
5. Q&A / Discussion

## Slide 40: [LVMWD] RO System Configuration and Measurement Points
P
・Feed Free Chlorine
・Feed Conductivity
・Feed pH, TOC, Temp
・Feed Pressure
・Feed Flow (Calc)
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Combined Permeate TOC
・Combined Permeate Conductivity
・Concentrate Pressure
・Concentrate Flow
・Inlet Free Chlorine
・Inlet Total Chlorine
・Inlet pH
・Inlet UVT
・Inlet Flow
UV
・Outlet Free Chlorine
・Outlet Total Chlorine
・Inlet UVT
・UV Dose
・UV Intensity
・UV Lamp Power (Constant 50%)
RO 1st Stage
RO 2nd Stage
RO 3rd Stage
Feed Pressure
Concentrate Pressure
Feed Pressure
P
This pump decides the feed flow to RO.
a
b
c
d
e
<Differential Pressure>
Stage 1 = －
Stage 2 = －
Stage 3 = －
a
b
b
c
d
e

## Slide 41
Index | Stage2 Permeate EC
RMSE | 2.46* (uS/cm)
MAPE | 5.59* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ② Stage2 Permeate EC ～

## Slide 42
Index | Stage3 Permeate EC
RMSE | 2.30* (uS/cm)
MAPE | 4.70* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ③ Stage3 Permeate EC ～

## Slide 43
Index | Stage2 Permeate EC
RMSE | 1.40* (uS/cm)
MAPE | 4.37* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ② Stage2 Permeate EC ～

## Slide 44
Index | Stage3 Permeate EC
RMSE | 2.02 (uS/cm)
MAPE | 4.06 (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ③ Stage3 Permeate EC ～

## Slide 45: 透過水質
トレンドを大まかに捉えているが、ECの予測値が実績よりも若干低い。
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
2.2 OCWD > 1st week 予測結果
Blue: Actual / Orange: Prediction
Actual Ave.: 0.055 [ppm],
Predict Ave.: 0.052 [ppm]
Actual Ave.: 23.48 [uS/cm],
Predict Ave.: 18.61 [uS/cm]
Actual Ave.: 2.22,
Predict Ave.: 2.24
Actual Ave.: 1.88,
Predict Ave.: 1.99

## Slide 46: 探索結果（最良解の推移）
実行可能解を得て、コストを改善する解が得られている。
2.2 OCWD > 1st week 最適化結果
10,000の半分で止めた
Blue: Objective Function Value /
Orange: Constraint Violation
約9分

## Slide 47: 操作計画：コスト変数と固定変数
Sulfuric Acid [ton/hour]（コスト）
S1流入圧力 [psi]（固定）
S1流入量 [gpm]（固定）
S1流入EC [uS/cm]（固定）
流入TOC [ppm]（固定）
Inhibitor [ton/hour] （コスト）
2.2 OCWD > 1st week 最適化結果
LRV基準の制約によって、Inhibitorが実績とほぼ同じ値になっている。
Blue: Actual / Orange: Optimized
Actual Ave.: 0.39 [ton/hour],
Optimized Ave.: 0.38 [ton/hour]
Actual Ave.: 0.0559 [ton/hour],
Optimized Ave.: 0.0560 [ton/hour]

## Slide 48: 操作計画：透過水質
ECのLRV基準の上限に位置する解となっている。
2.2 OCWD > 1st week 最適化結果
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
Actual Ave.: 0.055 [ppm],
Optimized Ave.: 0.053 [ppm]
Actual Ave.: 23.5 [uS/cm],
Optimized Ave.: 18.7 [uS/cm]
Actual Ave.: 2.22,
Optimized Ave.: 2.23
Actual Ave.: 1.88,
Optimized Ave.: 1.98

## Slide 49: コスト換算
約47$/day(18K$/year, 2.5M\/year)の削減効果と見積もれる。
  ただし、この条件では、ほぼ改善の余地が無いと見積もれる。
2.2 OCWD > 1st week 最適化結果
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err. | Cost [$/day]
Acid [ton/hour] | 0.39 | 0.38 | - 0.009 |  | - 0.009 | - 53.3
Inhibitor [ton/hour] | 0.0559 | 0.0560 | + 0.0001 |  | + 0.0001 | + 6.22
EC [uS/cm] | 23.5 | 18.7 | - 4.74 | - 4.87 | + 0.13 | 
TOC [mg/L] | 0.055 | 0.053 | - 0.002 | - 0.003 | + 0.001 | 
LRV EC | 1.88 | 1.98 | + 0.30 | - 0.01 | - 0.003 | 
LRV TOC | 2.217 | 2.234 | + 0.02 | + 0.02 | - 0.005 | 
Total |  |  |  |  |  | - 47.1