## Slide 1: NAWI RO Analysis Progress Report
W. Kumagai, H. Soya, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
June 22th, 2023
SGDC

## Slide 2: Self Introduction
Name
  Hiroaki Soya
Entering year
  2018
Department
  MK HQ INV Pjt Design Dept. Operational Excellence Gr.
  Supervisor : Kamada-san
Specialty
  Control Engineering

## Slide 3: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 4: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 5
3 Stages configuration and Toray’s TM720-370 is deployed
  Data Period
    Three years of data since 2020 are available.
    Provided minute interval data were converted to 30minutes trends.
RO
UF
Potable Water
UV／AOP
measuring point
P
pump
1. RO Permeate Water Quality Prediction
①Overall view of RO system

## Slide 6
Predictive modeling of RO permeate water quality was created.
Prediction Targets
  ①Stage1 Permeate EC ②Stage2 Permeate EC ③Stage3 Permeate EC ④Permeate TOC
RO system
measuring point
P
pump
Target①
Target②
Target③
Target④
1. RO Permeate Water Quality Prediction > Water Quality Model Concept
Water Quality Model Prediction Targets
※Conductivity = EC

## Slide 7
Model Concept
  Permeate EC Model Measured at each Stage → Build a model at each Stage
  Permeate TOC Model Measured at one location before and after RO system branching and merging → Build one model for the entire RO system
Permeate EC Model
Permeate TOC Model
Stage 1
Stage 2
Stage 3
Feed
Conc = 2nd Feed
Perm
Feed
Conc = 3rd Feed
Perm
Feed
Conc
Perm
①Stage1 Permeate EC
②Stage2 Permeate EC
③Stage3 Permeate
④Permeate TOC
RO system
Feed
Conc
Perm
Water Quality Model Concept
7
1. RO Permeate Water Quality Prediction ②Water Quality Model Concept

## Slide 8
Model: Multiple Regression Model
Used Variables
Variable Name | Stage1 Permeate EC | Stage2 Permeate EC | Stage3 Permeate EC | Permeate TOC
RO Stage 1 Feed Pressure | X |  |  | X
RO Feed EC | X |  |  | X
RO Feed Flow* | X |  |  | X
RO Feed Temperature | X | X | X | X
RO Feed pH | X |  |  | X
UF Filtrate Total Chlorine | X | X | X | X
RO Stage 2 Feed EC* |  | X |  | 
RO Stage 2 Feed Flow* |  | X |  | 
RO Stage 3 Feed Pressure |  |  | X | X
RO Stage 3 Feed EC* |  |  | X | 
RO Stage 3 Feed Flow* |  |  | X | 
RO Feed TOC |  |  |  | X
Water Quality Model Overview
1. RO Permeate Water Quality Prediction ②Water Quality Model Concept

## Slide 9
Data Period of Use ：July 1st, 2021 ~ July 27th, 2022
Build the model sequentially (Training and Prediction period：1 week each)
Data Preprocessing
  Removing Outliers
  Noisy Data Imputation
  Missing Data Imputation
Term | Training Period | Prediction Period
1 | from July 1st to July 7th, 2021 | from July 8th to July 14th, 2021
2 | from July 8th to July 14th, 2021 | from July 15th to July 21st, 2021
54 | from July 7th to July 13th, 2022 | from July 14th to July 20th, 2022
55 | from July 14th to July 20th, 2022 | from July 21st to July 27th, 2022
Term | Training Period | Prediction Period
1 | from July 1st to July 7th, 2021 | from July 8th to July 14th, 2021
2 | from July 8th to July 14th, 2021 | from July 15th to July 21st, 2021
54 | from July 7th to July 13th, 2022 | from July 14th to July 20th, 2022
55 | from July 14th to July 20th, 2022 | from July 21st to July 27th, 2022
Verification Overview
1. RO Permeate Water Quality Prediction ②Water Quality Model Concept

## Slide 10
Index | Stage1 Permeate EC | Stage2 Permeate EC
RMSE | 2.07 [uS/cm] | 2.36 [uS/cm]
MAPE | 5.27 [%] | 5.04 [%]
1. RO Permeate Water Quality Prediction ③Result
Stage1 Permeate EC and Stage2 Permeate EC

## Slide 11
Sequential model building allowed for adequate forecasting.
Because the study period is just before the evaluation period, trend tendencies are often similar
Periods with periodic trends
Periods with no periodic trend
1. RO Permeate Water Quality Prediction ③Result
Stage1 Permeate EC Prediction Trends

## Slide 12
Index | Stage3 Permeate EC | Permeate TOC
RMSE | 4.63 [uS/cm] | 0.030 [mg/L]
MAPE | 9.04 [%] | 19.46 [%]
1. RO Permeate Water Quality Prediction ③Result
Stage3 Permeate EC and Permeate TOC

## Slide 13
Problem
Insufficient treatment of outliers
Solution
To implement other outlier handling methods
To query the detection limits and sensitivity of the Measuring instrument
  Measured data of permeate TOC appear instantaneously with large changes in value. → There is a need to make appropriate decisions on whether or not an outlier.
1. RO Permeate Water Quality Prediction
Future Tasks

## Slide 14: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 15: 2. RO Membrane Fouling Modeling Problem Settings
Blockage Classification
  Scaling
    chemical dynamics
  Fouling
    Physical (fluidic) Dynamics
Supplementary
  system of units
    converting to the SI unit system e.g. Flow Rate : [gpm] to [m^3/s]
  Preprocessing
    using 12 [hour] moving average
target of this presentation

## Slide 16: 2. RO Membrane Fouling Modeling Physical Dynamics based Modeling
Theory：Bernoulli's principle
https://www.vedantu.com/physics/bernoullis-theorem

## Slide 17: 2. RO Membrane Fouling Modeling Physical Dynamics based Modeling
Definition of system input and output

## Slide 18: 2. RO Membrane Fouling Modeling Application to LVMWD
Bernoulli's Principle
  Exchanging volume flow to velocity
  Bernoulli’s principle at RO System
energy loss fouling?
Future work：Considering fluid of mass at each pipes

## Slide 19: 2. RO Membrane Fouling Modeling Modeling
Step1 : Estimate ρ,A from data
  Estimate using least squares
LVMWD
OCWD
measured
measured
calc
(equation of continuity)

## Slide 20: 2. RO Membrane Fouling Modeling Modeling
Step2 : Calculate
  Calculate using
  Normalize into 0-1
estimated
calc & measured

## Slide 21: 2. RO Membrane Fouling Modeling Future Works
Modeling Dynamics
  including the followings in Bernoulli's principle
    Buster Pump
    fluid of mass at each pipes
  Focus to 1st stage RO membrane
Estimation
  Using conductivity as a factor to estimate density ρ
SV vs
  Formulating the relationship between the estimated and the input of chlorine(SV) in order to optimize operation.

## Slide 22: Agenda
RO Permeate Water Quality Prediction
RO Membrane Fouling Modeling
RO Optimization Concept
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO Permeate Water Quality Prediction, second part is RO Membrane Fouling Modeling, third part is RO Optimization Concept. We’ll have a Q&A in final part. If you have any questions, please save them until the end.

## Slide 23: Scheduling Optimization
RO optimization problem is formulated into a scheduling optimization.
The procedure consists of below steps.
3. RO Optimization Concept
A
B
C
Facility Model
: Optimization Variable
1. Drawing Flow Chart
(Operational Cost)
(Facility Characteristics)
2. Formulation
Optimization Problem
Time
Operational Cost is $XX.
3. Calculation
Operational Schedule
Sample Flow Chart

## Slide 24: Flow Chart for RO Optimization: RO Total Part
3. RO Optimization Concept > Flow Chart
UF Filtrate Total Chlorine
ID000
ID001
ID002
cost
Feed EC
Feed TOC
Permeate TOC Prediction Model
Permeate TOC
RO Feed
ID004
S1 Feed Press
RO Total
ID4000
S1 Feed Flow
ID003
Feed pH
RO Stage1
Feed Temperature
ID100
ID101

## Slide 25: Flow Chart for RO Optimization: RO Each Stage Part
3. RO Optimization Concept > Flow Chart
S1_Perm_EC
S1 Permeate EC
RO Stage1
RO Stage2
RO Stage3
S2 Feed EC
ID1000
S2_Feed_EC
ID2000
S2_Perm_EC
ID2001
S3_Perm_EC
ID3001
RO Feed
S1 Feed Press
ID1000
S1 Feed Flow
S1 Perm Flow
S2 Permeate EC
ID100
ID101
ID102
S2 Feed Flow
S2 Perm Flow
S3 Feed Press
S3_Feed_EC
S3 Permeate EC
ID200
ID201
ID2001
S3 Feed EC
ID3000
S2 Perm EC
S1 Perm EC
UF Filtrate Total Chlorine
ID000
ID001
ID002
cost
Feed EC
Feed TOC
ID004
ID003
Feed pH
Feed Temperature
ID300
S3 Feed Flow
ID301

## Slide 26: Variable List
3. RO Optimization Concept > Problem Formulation
Notes: The objective can be subdivided into the following three steps. First step is considering~, to reduce excessive~. Second step is considering ~ that is monitoring the clogging, to clean when the clogging status~. Third step is considering ~ that is the life extension, to~. First stage can be rephrased as optimization of membrane condition fixed. On the contrary, Second and third steps can be rephrased as monitoring membrane condition taking advantage of optimization.

## Slide 27: Problem
3. RO Optimization Concept > Problem Formulation
Fluctuation range limit
Prediction Model
Objective Function
Constraint Conditions
Fixed Parameter
Intermediate Variable
Upper or Lower limit
Water Quality Standards
Logarithmic Reduction Value (LRV):
Notes: The objective can be subdivided into the following three steps. First step is considering~, to reduce excessive~. Second step is considering ~ that is monitoring the clogging, to clean when the clogging status~. Third step is considering ~ that is the life extension, to~. First stage can be rephrased as optimization of membrane condition fixed. On the contrary, Second and third steps can be rephrased as monitoring membrane condition taking advantage of optimization.

## Slide 28: Question (SGDC to INV)
3. Q&A / Discussion

## Slide 30: Supplementary Physical Dynamics based Modeling
Using Data
[mg/L Cl2]
RO Feed Free Chlorine
[mg/L Cl2]
UF Filtrate Total Chlorine
RO Stage 3 Concentrate Pressue
[psi]
RO Stage 3 Concentrate Flow
[psi]
[gpm]
RO Stage 1 Feed Pressure

## Slide 31: Analysis stance
In anticipation of the development of optimization, consider which data groups should be emphasized.
System
Input/Manipulated
parameter
Output quality
Disturbance
Expressing the input-output relationship of equipment as a characteristic formula
Quality
Time t
Time t
Comply with demand and quality required
Disturbance
Time t
Reduce operating costs
Identify disturbances
Formulation for operation planning optimization
Modeling with operational optimization in mind
Calculate the lowest cost operation plan within constraint conditions
Constraints and costs that need to be considered in operation are defined as formulas.
Expressing the input-output relationship of equipment as a characteristic formula
: Comply with the water quality.
: Reduce operating costs
: Each parameters should comply with the characteristic
Data-driven highlighted
Supplementary: RO Analytical Policy
Cost

## Slide 32: Difference per Objective
Step up from (small, easy) to (large, difficult).
Optimization effect
Small
Middle
Large
Optimization period
Short-term
(minutes to hours)
Mid-term
(days to months)
Long-term
(months to years)
Model strategy
Closer to statistical models
Statistical/ Physical Models
Closer to the physical model
Difficulty
Easy
Middle
Difficult
(1) 最終水質と供給量を考慮
(2) RO膜閉塞状態も考慮
(3) RO膜劣化も考慮
(1) Consider water quality and flow rate in Post-RO
(2) Consider RO Clogging
(3) Consider RO Deterioration
Supplementary: RO Analytical Policy
Notes: This slide shows the procedure of RO analysis. We plan to step up from small and easy to large and difficult. There are two reasons. First reason is time-span and period in optimization. Second reason is model strategy.

## Slide 33
[psi]
[psi]
[psi]
Supplementary: LVMWD Data RO Analysis
Pressure Trend (Feed)

## Slide 34
34
[psi]
[psi]
[psi]
[psi]
[psi]
Supplementary: LVMWD Data RO Analysis
Pressure Trend (Permeate, 2nd and 3rd Stage Concentrate)

## Slide 35
35
[gpm]
[gpm]
RO Stage Feed Flow Rate [gpm]
1
Supplementary: LVMWD Data RO Analysis
Flow Rate Trend (Feed)

## Slide 36
36
Supplementary: LVMWD Data RO Analysis
Flow Rate Trend (Permeate)
RO Stage Permeate Flow Rate [gpm]
1
RO Stage Permeate Flow Rate [gpm]
2
RO Stage Permeate Flow Rate [gpm]
3