## Slide 1: NAWI RO Analysis Progress Report
M. Kawata, W. Kumagai, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
February 1st, 2023
SGDC

## Slide 2: Agenda
RO Analytical Policy
LVMWD RO Data Analysis
Q&A / Discussion
Notes: This is today’s agenda. There are three parts, first part is RO analytical policy, I will explain. Second part is Lasvergenes RO Data Analysis, Imoto-san explain. Final part is Q&A/discussion part.

## Slide 3: Objective of RO Optimization
Operating costs are minimized considering RO membrane condition within the range of maintaining water quality and flow rate.
  Maintaining high recovery rate, good water quality (high salt rejection), and extending RO membrane life.
1. RO Analytical Policy
Clogging due to fouling Scaling by crystallization Bio-fouling by deposit
RO
Disinfection/ NaClO
UF
Clogging Prevention/ Anti-Scalant
Potable Water
Chemical Costs
Membrane Cleaning Costs
Water quality and flow rate to be maintained
UV／AOP
Electricity Costs
Control Carcinogens
Chemical Costs
Chemical Costs
Membrane Replacement Costs
Oxidation/
UV radiation with Chemical
Notes: First, I explain RO data analysis and optimization policy. This shows potable water reuse process. Water from sewage plant is treated by this process and supplied to potable reuse.
It mainly consists of UF, RO, UV, and AOP process units. The objective of RO optimization shows operating costs are ~. There are important costs in many places, for example, chemical cost, RO membrane cleaning cost, and electricity cost. Moreover, there are considering conditions in many places, for example, recover rate, water quality, and RO membrane life. So, optimization strategy is to select critical costs and conditions according to priority.

## Slide 4: Subdivided Objective
The objective can be subdivided into the following three steps.
（3）Considering deterioration of RO membrane (the life extension)
（1）Considering permeate water quality and feed flow
（2）Considering clogging status of RO membrane (monitoring the clogging)
Reduce excessive chemical dosage to meet water demand
Cleaning when the clogging status reaches the criteria limit rather than periodically (reduces excessive chemical cleaning)
Continue operation until replacement criteria based on expecting life
(Prevent unnecessary replacement)
(How continue operation and extent to the life if deterioration is severe, etc.)
Optimization of membrane condition fixed
Monitoring membrane condition taking advantage of optimization
1. RO Analytical Policy
Notes: The objective can be subdivided into the following three steps. First step is considering~, to reduce excessive~. Second step is considering ~ that is monitoring the clogging, to clean when the clogging status~. Third step is considering ~ that is the life extension, to~. First stage can be rephrased as optimization of membrane condition fixed. On the contrary, Second and third steps can be rephrased as monitoring membrane condition taking advantage of optimization.

## Slide 5: Focused Region
Expand the control and considered value step by step.
  Fix to the actual value when optimization calculation if the value is not considered
RO
NaClO
UF
Acid
Potable Water
UV / AOP
UV Radiation with H2O2 or NaClO
Anti-Scalant
Water Quality
(1) Considering permeate water quality and feed flow
Degree of Clogging
Membrane Cleaning
Membrane Life
Monitoring membrane status
1. RO Analytical Policy
Given Region
Given Region
Non-Monitoring membrane status
Subject to be optimization target if interchangeable with RO.
(2) Considering clogging status of RO membrane (monitoring the clogging)
(3) Considering deterioration of RO membrane (the life extension)
Notes: Based on the steps, RO analytical policy is to expand the control and considered value step by step. First step is to control and consider yellow values. Green values are added in second step and red values are added in third step as well. But gray regions are considered as given area in RO optimization, so they are fixed to actual value when calculation.

## Slide 6: Objective (1): Operation considering permeate water quality and feed flow
Optimization: Reduce chemical costs within the balance of water quality and flow rate in Pre & Post-RO.
Modeling: Predict Post-RO water quality and flow rate based on Pre-RO data.
Post-RO
Water Quality
Pre-RO
Water Quality and Flow Rate
Time
Time
1. RO Analytical Policy
RO
NaClO
UF
UV / AOP
UV Radiation with
H2O2 or NaClO
Acid
Potable Water
Anti-Scalant
Water Quality
Degree of Clogging
Membrane Cleaning
Membrane life
Flow rate should be constant.
Given Region
Given Region
Predict water quality
Decide operation values
Prediction Model
Optimization Model
Notes: We are trying the first step now. This is an overview in first step. Optimization is to reduce chemical costs ~ Post-RO. And modeling is to predict ~. Please have a look at the lower figure. Left is water quality and flow rate in pre-RO. We try to predict water quality in post-RO from left data. After that, we try to decide the best operation values from right data by optimization. So, we need to build the quality prediction model and optimization model. This is the end of the explanation of RO analytical policy. I’ll switch to Imoto-san.

## Slide 7: Agenda
RO Analytic Policy
LVMWD RO Data Analysis
  Data Description
  Focus Points
  Result
  Future Tasks
Q&A / Discussion
Notes: Next, I would like to talk about the LasVirgenes (Municipal Water District) RO Data Analysis.
This part consists of 4 topics,
①Data Description ②Focus Points ③Result ④Future Tasks.

## Slide 8: Overall view of RO system
2. LVMWD Data RO Analysis ①Data Description
3 Stages configuration and Toray’s TM720-370 is deployed
  Data Period
    Three years of data since 2020 are available.
    Provided minute interval data were converted to daily trends.
RO
UF
Potable Water
UV／AOP
measuring point
P
pump
Notes: Now, Let’s start with Data Description. First is overall view of the RO membrane system of Las Virgenes.
The RO system of Las Virgenes consists of three stages, 1st, 2nd, 3rd stage from the upstream.
RO membranes are Toray’s TM720-370.
〇×marks are the measuring point. They collect the data like pressure, conductivity, TOC and so on.
〇P indicates the place of pump.
About three years data from 2020 are available. We converted minute data to daily trend.
Through the daily trend, we wanted to see the long-term trend of each variable.

## Slide 9: Calculation Tag
2. LVMWD Data RO Analysis ①Data Description ②Focus Points
1st Stage DP = 1st Stage Feed Pressure – 2nd Stage Feed Pressure
2nd Stage DP = 2nd Stage Feed Pressure – 2nd Stage Concentrate Pressure
3rd Stage DP = 3rd Stage Feed Pressure – 3rd Stage Concentrate Pressure
Focus Points
Differential Pressure between modules
TOC Removal Ratio
Conductivity
Notes: Next is Focus Points on the analysis.
We select 3 key data, ① Differential Pressure between modules ②TOC Removal Ratio ③Conductivity.
Firstly, we calculate 1st Stage DP, 2nd Stage DP and 3rd DP.
1st Stage DP equals 1st Stage Feed Pressure – 2nd Stage Feed Pressure.
2nd Stage DP equals 2nd Stage Feed Pressure – 2nd Stage Concentrate Pressure.
3rd Stage DP equals 3rd Stage Feed Pressure – 3rd Stage Concentrate Pressure.
Secondly, we calculate TOC Removal Ratio.
TOC Removal Ratio is Feed TOC at RO 1st stage – combined permeate TOC divided by Feed TOC at RO 1st stage (multiplied by) 100.
It is an indicator for checking water quality on site.
Thirdly, we focus on conductivity.

## Slide 10: Differential Pressure between modules
2. LVMWD Data RO Analysis ③Result
  DP trends change before and after the maintenance event like CIP. However, information is not clear to identify the event.
  While the CIP interval, DP decay is limited in 0.1 psi/month, 1.5%/month based on 2022.
RO 1st Stage DP [psi]
RO 2nd Stage DP [psi]
RO 3rd Stage DP [psi]
Notes: Next is analysis Result.
First is about Differential Pressure between modules.
There is the trend of DP, from left to right: 1st Stage DP, 2nd Stage DP, 3rd Stage DP.
Vertical axis is DP. Horizontal axis is date.
The red dotted line is assumed to be the timing of maintenance.
These trends show that DP trends change before and after the maintenance event like CIP.
However, information is not clear to identify the event.
While the CIP interval, DP decay is limited in 0.1 psi/month, 1.5%/month based on 2022.

## Slide 11: TOC Removal Ratio
2. LVMWD Data RO Analysis ③Result
  TOC Removal were approximately 98.89 ± 0.95%.
  The data below 99% were also scattered, and the reason and necessity of verification are not clear.
TOC Removal Ratio [%]
Notes: Second is about TOC Removal Ratio.
This is the trend of TOC Removal Ratio.
Vertical axis is TOC Removal Ratio. Horizontal axis is date.
TOC Removal Ratio were approximately 98.89 ± 0.95%.
The data below 99% were also scattered, and the reason and necessity of verification are not clear. We need to clarify.

## Slide 12: Conductivity
2. LVMWD Data RO Analysis ③Result
Flat
These trends suggest the possibility that RO membrane clogging is progressing.
Increased conductivity
＝ Deterioration of water quality （ Green area：after June in 2022）
Permeate side
Supply side
Constant conductivity
= no change in water quality
Notes: Third is Conductivity.
This trend in orange area is data of supply side that is RO 1st Feed Conductivity.
These trends in blue area are data of permeate side that are RO 1st Stage Permeate Conductivity, RO 2nd Stage Permeate Conductivity and RO 3rd Stage Permeate Conductivity.
RO 1st Feed Conductivity have remained flat.
Constant conductivity means that the water quality is not change.
On the other hand, trends in blue area that are 1st Stage Permeate Conductivity, RO 2nd Stage Permeate Conductivity and RO 3rd Stage Permeate Conductivity increase after June in 2022 that displayed by green area.
Increasing conductivity means water quality is deterioration.
According to these treads, there is the possibility that RO membrane is clogged.

## Slide 13: Sulfuric Acid and Anti-scalant
  Sulfuric Acid and Anti-Scalant are constant values.
2. LVMWD Data RO Analysis ③Result
RO Sulfuric Acid Dosing Setpoint
Anti-scalant Dosing Pump
Notes: Next is about Sulfuric Acid(アセッド) and Anti-scalant.
In the site, they use two types of chemical dosage, one is Sulfuric Acid and the other is Anti-scalant.
Left side is RO Sulfuric Acid Dosing trend.
Right side is Anti-scalant Dosing trend.
Both have remained flat.

## Slide 14: RO 1st Stage Feed Pressure and RO 1st Stage Permeate Conductivity
2. LVMWD Data RO Analysis ③Result
  The correlation between RO 1st Stage Feed Pressure and RO 1st Stage Permeate Conductivity is negative. (April to July in 2022) → It matches the theoretical behavior of RO membrane.
Notes: Next is about the correlation.
We check the correlation between RO 1st Stage Feed Pressure and RO 1st Stage Permeate Conductivity. We use the data from April to July in 2022.
This figure show that the correlation is negative.
It matches the theoretical behavior of RO membrane.

## Slide 15: Future Tasks
Analysis of other data and construction of water quality predicting and optimization models.
2. LVMWD Data RO Analysis
Water quality prediction / optimization modeling
Viscosity of water at temperature
Chemical dosage
Predict water quality and flow rate and decide values
Post-RO
Water quality and flow rate
Pre-RO
Water quality and flow rate
Time
Time
Prediction
Optimization
the salt rejection
Re-examine the way of analysis
because of constant chemical dosage
Focusing the salt rejection for driving pressure
at each stages from 1st to 3rd
Adding water viscosity variables
Notes: Finally, I would like to talk about future tasks.
We will analyze other data and construct water quality prediction and optimization models.
The three points are under consideration, ①viscosity of water at temperature ②Chemical dosage ③the salt rejection.
We share the concrete image of water quality prediction and optimization modeling.
Please look at the right side of the slide.
First, prediction model.
We predict the Post-RO Water quality and flow rate from Pre data of that.
Second, optimization modeling.
We decide values of control (like how much chemical, we add, how to change the pressure) under the stander of Post-RO Water quality and flow rate (for example, adapting to law regulation).
That’s all. Thank you for listening.

## Slide 16: Question (SGDC to INV)
SGDCから質問を受け付ける
3. Q&A / Discussion

## Slide 17: Question (INV to SGDC)
SAO Algorithm for UF Process（熊谷、必要性は下がるが）
3. Q&A / Discussion

## Slide 19: Analysis stance
In anticipation of the development of optimization, consider which data groups should be emphasized.
System
Input/Manipulated
parameter
Output quality
Disturbance
Expressing the input-output relationship of equipment as a characteristic formula
Quality
Time t
Time t
Comply with demand and quality required
Disturbance
Time t
Reduce operating costs
Identify disturbances
Formulation for operation planning optimization
Modeling with operational optimization in mind
Calculate the lowest cost operation plan within constraint conditions
Constraints and costs that need to be considered in operation are defined as formulas.
Expressing the input-output relationship of equipment as a characteristic formula
: Comply with the water quality.
: Reduce operating costs
: Each parameters should comply with the characteristic
Data-driven highlighted
Supplementary: RO Analytical Policy
Cost

## Slide 20: Difference per Objective
Step up from (small, easy) to (large, difficult).
Optimization effect
Small
Middle
Large
Optimization period
Short-term
(minutes to hours)
Mid-term
(days to months)
Long-term
(months to years)
Model strategy
Closer to statistical models
Statistical/ Physical Models
Closer to the physical model
Difficulty
Easy
Middle
Difficult
(1) 最終水質と供給量を考慮
(2) RO膜閉塞状態も考慮
(3) RO膜劣化も考慮
(1) Consider water quality and flow rate in Post-RO
(2) Consider RO Clogging
(3) Consider RO Deterioration
Supplementary: RO Analytical Policy

## Slide 21: Data List
 | variable | Measurement |  | variable | Measurement | 種類 | variable | Measurement
Pressure | 1st Feed | actual | Flow rate | 1st Feed | Cal | Conductivity | 1st Feed | actual
 | 1st Permeate | actual |  | 1st Permeate | actual |  | 1st Permeate | actual
 | 2nd Feed | actual |  | 2nd Feed | Cal |  | 2nd Permeate | actual
 | 2nd Permeate | actual |  | 2nd Permeate | actual |  | 3rd Permeate | actual
 | 2nd Concentrate | actual |  | 2nd Concentrate | actual | TOC | 1st Feed | actual
 | 3rd Feed | actual |  | 3rd Feed | Cal |  | Combined Permeate | actual
 | 3rd Permeate | actual |  | 3rd Permeate | actual |  |  | 
 | 3rd Concentrate | actual |  | 3rd Concentrate | actual |  |  | 
DP | 1st DP | Cal |  |  |  |  |  | 
 | 2nd DP | Cal |  |  |  |  |  | 
 | 3rd DP | Cal |  |  |  |  |  | 
Supplementary: LVMWD Data RO Analysis

## Slide 22
[psi]
[psi]
[psi]
Supplementary: LVMWD Data RO Analysis
Pressure Trend (Feed)

## Slide 23
23
[psi]
[psi]
[psi]
[psi]
[psi]
Supplementary: LVMWD Data RO Analysis
Pressure Trend (Permeate, 2nd and 3rd Stage Concentrate)

## Slide 24
24
[gpm]
[gpm]
RO Stage Feed Flow Rate [gpm]
1
Supplementary: LVMWD Data RO Analysis
Flow Rate Trend (Feed)

## Slide 25
25
Supplementary: LVMWD Data RO Analysis
Flow Rate Trend (Permeate)
RO Stage Permeate Flow Rate [gpm]
1
RO Stage Permeate Flow Rate [gpm]
2
RO Stage Permeate Flow Rate [gpm]
3

## Slide 26: 今後の課題
他データの分析と、水質予測モデルや最適化モデルの構築。
2. LVMWD RO Analysis
水質予測／最適化モデルの構築
流量の温度補正
薬液添加量
水質基準などを守る範囲で、
薬液添加量や圧力操作を決定
膜後の水質
膜前のデータ
時間
時間
予測
最適化
流量が一定の図
温度補正された流量イメージ
塩分除去率