Project Title: NAWI TASK 5.17 - (Salveson, Andy) Data-Driven Fault Detection and Process Control for Potable Reuse with Reverse Osmosis

PROGRESS AND STATUS BY SUBTASK:

Task: Task 5.17.1 – Desktop Evaluations

Task: Subtask 5.17.1.5 – Data-Driven Model Optimization (DDMO) for Chloramine and Anti-Scalant Dosing

Subtask Lead: Steve Hayden

Research Questions:

- How much cost and energy could be saved across the reuse treatment train applying DDMO to adjust the pre-chloramine and antiscalant doses and predict a fault in real-time in response to water quality changes?

PROGRESS AND STATUS:

- Collected data from:

  - Las Virgenes Municipal Water District

    - All necessary data is available and shared among the team

  - Orange County Water District

    - All necessary data is available and shared among the team

  - West Basin Municipal Water District

    - Additional data from WBMWD is still needed.

【下記、Q3の構成】

Budget Spent (YCA)

Summary (Kawata-san)

In Task 5.17.1.5, data driven model optimization is used to optimize chloramine and anti-scalant dosing ahead of RO. In this report, we report data analysis underway for the model creation based on OCWD’s full scale plant and LVMWD’s demonstration plant. A key study objective is chemical optimization (e.g., anti-scalant) in the RO operation at both plants.

...

Desktop Evaluation based on OCWD (Operational Excellence Gr.)

- Water Quality Prediction (Imoto-san)

- RO Membrane Scaling using Xact Data (Soya-san)

濃度分極モデルと計算結果

- RO Optimization Simulation Model (Kumagai)

- Summary

We formulated RO optimization problem for OCWD and constructed a RO optimization simulation model implemented by the water quality prediction or scaling model. We will carry out the optimization simulation and calculate an improvement effect compared actual operation in the past period in the final report.

- RO Optimization Problem for OCWD

Basic optimization story for OCWD is to decrease the chemical dosing cost (e.g., antiscalant or pH adjustors) while satisfying water quality standards or monitoring a RO membrane scaling. Considering the above story, we formulated the RO optimization problem for OCWD.

- Scheduling Problem

RO optimization is to improve the operation in some period of time. This type of optimization problem is the scheduling problem, which is formulated and solved according to procedure as shown in Figure 1.1. The procedure consists of drawing flow chart, formulation mathematical optimization problem, and calculation operational schedule. Therefore, drawing a flow chart, variable, objective function, and constraint condition are required to construct a simulation model.

The operational schedule structure is shown as Table 1.1. xit denotes the i-th variable schedule at time t, xi=(xi1, xi2,…, xiL) denotes the i-th variable schedule in all period, X=(x1,x2,…,xn) denotes all variables schedule in all period, L denotes the length of the optimization period, and n denotes the number of variables, respectively.

Figure 1.1: Procedure for Solving Scheduling Problem

Table 1.1: Operational Schedule Structure (OCWD)

|  | x1[t] | x2[t] | ⋯ | xn[t] |
| --- | --- | --- | --- | --- |
| t=1 | x1[1] | x2[1] | ⋯ | xn[1] |
| t=2 | x1[2] | x2[2] | ⋯ | xn[2] |
| ⋯ | ⋯ | ⋯ | ⋯ | ⋯ |
| t=L | x1[L] | x2[L] | ⋯ | xn[L] |

- Flow Chart

Figure 1.2 shows the flow chart for OCWD based on the RO system configuration. The RO system configuration of OCWD can be found in Additional Materials A1. This flow chart includes the prediction model in the previous section.

Figure 1.2: Flow Chart for RO Optimization Simulation (OCWD) [TBD]

- Mathematical Optimization Problem

Mathematical optimization problem is formulated as minimizing f(x) such that constraints gκx≤0 (κ=1,2,…,K), where x∈RN denotes the optimization variable, f:RN→R denotes the objective function (cost function), gκ:RN→R denote K constraint functions, R denotes the set of real numbers, N denotes the number of total variables, respectively.

Optimization variable list is as shown in Table 1.2. Optimization variable denotes cost variable (chemical dose), fixed parameter denotes actual value in the calculation, intermediate variable denotes variable indirectly affecting objective function or constraints in the calculation (e.g., prediction value).

Table 1.2: Optimization Variable List (OCWD)

| ID No. | Description | Opt. Variable / Fixed Parameter |
| --- | --- | --- |
| ID0000 | Sulfuric Acid Usage | Optimization Variable |
| ID0001 | Threshold Inhibitor Usage | Optimization Variable |
| ID0002 | Feed Conductivity | Fixed Parameter |
| ID0003 | Feed TOC | Fixed Parameter |
| ID0004 | Feed Temperature | Fixed Parameter |
| ID0005 | Feed pH | Fixed Parameter |
| ID0100 | S1 Feed Pressure | Fixed Parameter |
| ID0101 | S1 Feed Flow Rate | Fixed Parameter |
| ID0200 | S2 Feed Pressure | Fixed Parameter |
| ID0201 | S2 Feed Flow Rate | Fixed Parameter |
| ID0300 | S3 Feed Flow Rate | Fixed Parameter |
| ID1000 | S1 Permeate EC | Intermediate Variable |
| ID2000 | S2 Feed EC | Intermediate Variable |
| ID2001 | S2 Permeate EC | Intermediate Variable |
| ID3000 | S3 Feed EC | Intermediate Variable |
| ID3001 | S3 Permeate EC | Intermediate Variable |
| ID4000 | Permeate TOC | Intermediate Variable |

The objective function f(x) is formulated as follows:

f(x) =t=1L(c1xID0000t+c2xID0001t)#1.1

Here, xID0000t denotes threshold inhibitor usage at time t, xID0001t denotes the sulfuric acid usage at time t, c1,c2 denotes cost coefficients, and L denotes the length of optimization period, respectively.

Constraint conditions are as following:

0≤xID0000t≤50;  t=1,2,…,L#1.2

0≤xID0001t≤50;  t=1,2,…,L#1.3

0≤xID1000t≤50;  t=1,2,…,L#1.4

0≤xID2001t≤50;  t=1,2,…,L#1.5

0≤xID3001t≤50;  t=1,2,…,L#1.6

0≤xID4000t≤50;  t=1,2,…,L#1.7

-1≤xID0000t-xID0000t+1≤1;  t=1,2,…,L-1#1.8

-1≤xID0001t-xID0001t+1≤1;  t=1,2,…,L-1#1.9

0≤γID1000t≤50;  t=1,2,…,L#1.10

0≤γID2001t≤50;  t=1,2,…,L#1.11

0≤γID3001t≤50;  t=1,2,…,L#1.12

0≤γID4000t≤50;  t=1,2,…,L#1.13

Here, Equations (1.2), (1.3), (1.4), (1.5), (1.6), (1.7) denotes lower and upper limit, Equations (1.8), (1.9) denotes fluctuation range limit, Equations (1.10), (1.11), (1.12), (1.13) denotes water quality standards limit, respectively.

xID1000t (Stage1 permeate conductivity), xID2001t (Stage2 permeate conductivity), , xID3001t (Stage3 permeate conductivity), and xID4000t (permeate TOC) are calculated by water quality prediction model as follows:

xID1000t=FID1000();  t=1,2,…,L#1.14

xID2001t=FID2001();  t=1,2,…,L#1.15

xID3001t=FID3001();  t=1,2,…,L#1.16

xID4000t=FID4000();  t=1,2,…,L#1.17

γX is Logarithmic Reduction Value (LRV) of water quality as follows:

γXt=log10Xfeed[t]Xperm[t];  t=1,2,…,L#1.18

Here, Xfeed denotes feed X and Xperm denotes permeate X at each stage.

The scale of the above problem can be roughly estimated. Number of total optimization variables N=2L and number of total constraints K=12L-2. For example, if the optimization period is 1week of 30 minutes time interval data, we can estimate L=48×7=336, N=2×336=672, and K=12×336-2=4030.

- Optimization Algorithm

The above problem is classified as constrained and black-box problem. We used an optimization algorithm combining SHADE and Feasibility Rule for solving the problem. SHADE is known to the best algorithm in the black-box optimization field recently and often used in the BBOB competition. We finished to write python source code from scratch and will apply it to the above problem.

Desktop Evaluation based on LVMWD (Operational Excellence Gr.)

- Water Quality Prediction (Imoto-san)

- RO Membrane Fouling (Soya-san)

ベルヌーイの定理から抵抗を算出するというコンセプト

- RO Optimization Simulation Model (Kumagai)

- Summary

We formulated RO optimization problem for LVMWD and constructed a RO optimization simulation model implemented by the water quality prediction or fouling model. We will carry out the optimization simulation and calculate an improvement effect compared actual operation in the past period in the final report.

- RO Optimization Problem for LVMWD

We formulated the RO optimization problem for LVMWD. Basic optimization story for LVMWD is to decrease the chemical dosing cost (e.g., chloramines) while satisfying water quality standards or monitoring a RO membrane fouling. The problem is formulated as scheduling problem same as OCWD.

- Flow Chart

Figure 2.1 shows the flow chart for LVMWD based on the RO system configuration. The RO system configuration of LVMWD can be found in Additional Materials A2. This flow chart includes the prediction model in the previous section.

Figure 2.1: Flow Chart for RO Optimization Simulation (LVMWD)

- Mathematical Optimization Problem

Optimization variables are as shown in Table 2.1. Optimization variable denotes cost variable (chemical dose), fixed parameter denotes actual value in the calculation, intermediate variable denotes variable indirectly affecting objective function or constraints in the calculation (e.g., prediction value).

Table 2.1: Optimization Variable List (LVMWD)

| ID No. | Description | Opt. Variable / Fixed Parameter |
| --- | --- | --- |
| ID0000 | UF Filtrate Total Chlorine | Optimization Variable |
| ID0001 | Feed Conductivity | Fixed Parameter |
| ID0002 | Feed TOC | Fixed Parameter |
| ID0003 | Feed Temperature | Fixed Parameter |
| ID0004 | Feed pH | Fixed Parameter |
| ID0100 | Stage 1 Feed Pressure | Fixed Parameter |
| ID0101 | Stage 1 Feed Flow Rate | Fixed Parameter |
| ID0200 | Stage 2 Feed Flow Rate | Fixed Parameter |
| ID0300 | Stage 3 Feed Pressure | Fixed Parameter |
| ID0301 | Stage 3 Feed Flow Rate | Fixed Parameter |
| ID1000 | Stage 1 Permeate EC | Intermediate Variable |
| ID2000 | Stage 2 Feed EC | Intermediate Variable |
| ID2001 | Stage 2 Permeate EC | Intermediate Variable |
| ID3000 | Stage 3 Feed EC | Intermediate Variable |
| ID3001 | Stage 3 Permeate EC | Intermediate Variable |
| ID4000 | Permeate TOC | Intermediate Variable |

The objective function f(x) is formulated as follows:

f(x) =t=1L(c1xID0000t)#2.1

Here, xID0000t denotes threshold inhibitor usage at time t, c1 denote cost coefficients, and L denotes the length of optimization period, respectively.

Constraint conditions are as following:

0≤xID0000t≤50;  t=1,2,…,L#2.2

0≤xID1000t≤50;  t=1,2,…,L#2.3

0≤xID2001t≤50;  t=1,2,…,L#2.4

0≤xID3001t≤50;  t=1,2,…,L#2.5

0≤xID4000t≤50;  t=1,2,…,L#2.6

-1≤xID0000t-xID0000t+1≤1;  t=1,2,…,L-1#2.7

0≤γID1000t≤50;  t=1,2,…,L#2.8

0≤γID2001t≤50;  t=1,2,…,L#2.9

0≤γID3001t≤50;  t=1,2,…,L#2.10

0≤γID4000t≤50;  t=1,2,…,L#2.11

Here, Equations (2.2), (2.3), (2.4), (2.5), (2.6) denote lower and upper limit, Equation (2.7) denotes fluctuation range limit, Equations (2.8), (2.9), (2.10), (2.11) denote water quality standards limit, respectively.

xID1000t (Stage1 permeate conductivity), xID2001t (Stage2 permeate conductivity), , xID3001t (Stage3 permeate conductivity), and xID4000t (permeate TOC) are calculated by water quality prediction model as follows:

xID1000t=FID1000();  t=1,2,…,L#2.12

xID2001t=FID2001();  t=1,2,…,L#2.13

xID3001t=FID3001();  t=1,2,…,L#2.14

xID4000t=FID4000();  t=1,2,…,L#2.15

γX is Logarithmic Reduction Value (LRV) of water quality same as Equation (1.18).

- Optimization Algorithm

We used SHADE and Feasibility Rule as optimization algorithm for solving the above constrained optimization problem same as OCWD.

Desktop Evaluation based on WBMWD (Kawata-san)

- Target Process for Data Analysis and Measurements Points

- Trend Charts

- Title 22 Requirements

- Predicting Turbidity from Title 22

Future Tasks (Kawata-san)

【下記、書式設定等】

特に指示されていないが、提出済レポートから参考にした。

[フォント]

・基本的に、フォントスタイルはTimes New Romanで、フォントサイズは12ptで統一する。

[章構成]

・各自で該当章を記入するが、内容や分量に応じて、追加で節・項などを挿入しても良い。ただし、「見出し」を設定しているため、Word上部「表示」タブ⇒「ナビゲーションウィンドウ」で段落のレベルを合わせる。

[図表]

・図表は、テキストボックスに挿入し、キャプションと共に管理する。テキストボックスは「文字列の折り返し」を「上下」にする。

・図表のキャプションのフォントはbold体とする。

・図表の位置は、ページの下部、または上部に寄せるように調整する。

・図表番号は、前から順にFigure1、Figure2、…と若い番号で割り当てていく（合体前は自分のパートだけで割り当てて良い）。ただし、図表の数は多くなりがちなので、類似の図はsubfigureとして一つにまとめる。

・jpegファイルをwordに貼ると、圧縮されて解像度が下がる。Word上部タブの「ファイル」⇒「オプション」⇒「詳細設定」⇒「ファイル内のイメージを圧縮しない」にチェックを入れることで防ぐ。（このファイルは設定済だが、一応書いておく）

・図の例を下記に示す。

[グラフのフォーマット]

・X軸ラベルとY軸ラベルを付ける。単位がある場合は単位も付す。（例：Feed Temperature [℃]）

・同じグラフに、複数種類のデータがある場合は、凡例を付ける。可能なら、単位がある場合は単位も付す。（例：Feed Temperature [℃]）

・X軸方向の目盛線とY軸方向の目盛線を追加する。

・X軸が日付なら「Date」とする。日付のフォーマットは、“dd-Month-yy”とする（2023/11/10なら、10-Nov-23）。pythonなら、datetimeオブジェクトをstrftime関数などで、英語表記に変更できる。

[数式]

・数式は画像で張り付けるのではなく、wordの数式エディタを用いる。Word上部「挿入」タブ⇒「数式」から挿入可能。

・数式番号は、前から順に(1)、(2)、…と若い番号で割り当てていく（合体前は自分のパートだけで割り当てて良い）。

・数式の例を下記に示す。

[付録（Additional Materials）]

・メインパートに全ての数式や図表を多く挿入するとメインにレポートしたい主張が見づらくなるため、補足的な数式や図表は全てAdditional Materialsに移す。

(a): 1st Stage Raw Conductivity       (b): 1st Stage Preprocessed Conductivity

(c): 2nd Stage Raw Conductivity       (d): 2nd Stage Preprocessed Conductivity

(e): 3rd Stage Raw Conductivity       (f): 3rd Stage Preprocessed Conductivity

Figure XX: Raw and Preprocessed Data of Permeate Conductivity in Each RO Stage [sample figure]

[sample mathematical formula]

The evaluation index is Mean Absolute Percentage Error (MAPE) EMAPE[%], which is a relative prediction error and formulated as follows:

EMAPE=100Lt=1LyPret-yActtyActt#12

Here, yActt is the actual data and yPret is the predicted data at time t. L is the length of the prediction period.

Additional Materials

A1) RO System Configuration (OCWD)

The data set provided to this team is for the 100 mgd system. We note that the capacity has recently been upgraded to 130 mgd. The full-scale RO membrane system in OCWD, for the longer running 100 mgd of capacity, consists of 21 RO units (3 RO units x 7 RO trains) and each unit has 5 MGD capacity. As OCWD reported in Figure XX, these 21 RO systems are being operated by different types of RO membranes. Current analysis focuses upon RO UNIT B01. As shown in the figure below, the membrane type of RO UNIT B01 is Filmtec BW30XFRLE installed in October 2020.

RO UNIT B01 is a 3-stage configuration, with flow rate, pressure, conductivity, and differential pressure measured as shown in the Figure XX. 50 categories of data were provided including feed & permeate flow rate, feed & permeate water qualities (such as conductivity, TOC, turbidity), feed & permeate pressure, Xact, and chemical dosage.

Figure XX: RO System Membranes (OCWD)

Figure XX: RO Unit B01 System Configuration (OCWD)

Figure XX: RO System Configuration (OCWD)

A2) RO System Configuration (LVMWD)

The RO membrane system in LVMWD is a pilot scale system. The RO system consists of 3-stage configuration, utilized the Toray TMG10D membrane, and is shown in the Figure XX.

Figure XX: RO System Configuration and Measurement Points (LVMWD)

A3) Temperature Correction Factor

Used mathematical equations for Temperature Correction Factor (TCF) or normalization in this report are as follows:

- Water Viscosity (Temperature dependency; Andrade equation): η

ηT=expcT+273.15#(A1)

Here, T[℃] is the water temperature and c is a specific coefficient. c=1965 in LVMWD data, c=3140 in OCWD data.

- Water Fluidity (Temperature dependency): φ

φT=1ηT#(A2)

Here, η is the water viscosity.

- Temperature Correction Factor (TCF): F

F(T)=ηTsηT#(A3)F(T)=φTsφT=ηTηTs#(A4)

Here, T[℃] is the water temperature and Ts=25[℃] is the standard temperature. Eq.(A3) is used in LVMWD data and Eq.(A4) is used in OCWD data.

- Temperature Correction Factor for Flow: QTCF

QTCF(T)=ηT×expc×T-Ts#(A5)c=0.0107, T≤250.0072,otherwise#(A6)

Here, η is the water viscosity, T[℃] is the water temperature and Ts=25[℃] is the standard temperature.

- Temperature Correction Factor for Salt: STCF

STCF(T)=expc×T-Ts#(A7)c=0.0331, T≤250.0289,otherwise#(A8)

Here, η is the water viscosity, T[℃] is the water temperature and Ts=25[℃] is the standard temperature.

- Net Driving Pressure (NDP)

PND=Ptrans-ΔPn+1-Δπ#(A9)Ptrans=Pfeed-Pperm#(A10)ΔP=Pfeed-Pbrine#(A11)

Here, Ptrans is the RO transmembrane pressure, ΔP is the differential RO module pressure, Δπ is the osmotic pressure, n is the number of RO stages in the system, Pfeed is the RO feed pressure, Pperm is the RO permeate pressure of entire train, and Pbrine is the RO brine pressure. Unit of each pressure is bar in LVMWD data and psi in OCWD data. n=1 in OCWD data.

- Average Osmotic Pressure Differential: Δπ

Δπ=OPfb-OPperm#(A12)OPfb=α×LMfb, TDS#(A13)OPperm=β×TDSperm#(A14)

Here, OPfb is the average of osmotic pressure between feed and brine flow, OPperm is the permeate osmotic pressure, LMfb, TDS is the log mean factor between feed and brine for TDS, TDSperm[ppm] is the permeate TDS, and α,β>0 are constant coefficients. Eq.(A12) is used in LVMWD.

- Log Mean Factor considering concentration polarization on RO surface: LMfb, TDS, LMbrine, C

LMfb, TDS=TDSbrine-TDSfeedlnTDSbrine-TDSfeed#(A15)LMbrine, C=ln11-RR#(A16)

Here, LMfb, TDS is the log mean factor between feed and brine for TDS, LMbrine, C is the log mean factor for brine concentration, TDSfeed is the feed TDS, TDSbrine is the brine TDS, and R is the recovery rate. Unit of each TDS is ppm in LVMWD data. Eq.(A15) is used in LVMWD data and Eq.(A16) is used in OCWD data.

- Recovery Rate: R

R=QpermQfeed#(A17)

Here, Qfeed is the RO feed flow rate and Qperm is the RO permeate flow rate.

- Average Feed and Brine Concentration: Cfb

Cfb=Cfeed×LMbrine, C#(A18)

Here, Cfeed is the RO feed concentration and LMbrine, C is the log mean factor for brine concentration.

- Average Feed and Brine Flow Rate: Qfb

Qfb=Qfeed+Qbrine2#(A19)Qfb=2×Qbrine+Qperm2#(A20)

Here, Qfeed is the RO feed flow rate, Qperm is the RO permeate flow rate, and Qbrine is the RO brine flow rate. Unit of each flow rate is gpm (gallon per minute) in LVMWD data and OCWD data. Eq.(A19) is used in LVMWD data and Eq.(A20) is used in OCWD data.

- Calculated TDS: TDSbrine,TDSfeed,TDSperm

TDSbrine=TDSfeed×Qfeed-TDSperm×QpermQbrine#(A21)TDSfeed=a×expb-lnμfeed2c#(A22)TDSperm=a×expb-lnμperm2c#(A23)

Here, TDSfeed is the RO feed TDS, TDSperm is the RO permeate TDS, TDSbrine is the RO brine TDS, Qfeed is the RO feed flow rate, Qperm is the RO permeate flow rate, and Qbrine is the RO brine flow rate. μfeed, μperm are conductivities. In Eqs.(A22) and (A23), a, b, c are constant coefficients and given by as follows:

a=8.01×10-11,Cfeed>76307.70×10-20,otherwise#(A24)b=-50.6458,Cfeed>7630-90.4756,otherwise#(A25)c=112.484,Cfeed>7630188.8844,otherwise#(A26)

where Cfeed[μS/cm] is the feed conductivity.

R. Tanabe and A. Fukunaga: “Success-History Based Parameter Adaptation for Differential Evolution,” Proceedings of IEEE Congress on Evolutionary Computation 2013, pp.71–78 (2013)

K. Deb: “An Efficient Constraint Handling Method for Genetic Algorithms”, Computer Methods in Applied Mechanics and Engineering, Vol. 186 No. 2-4, pp.311-338 (2000)

The Black-box Optimization Benchmarking (BBOB) workshop series (https://numbbo.github.io/workshops/)

GWRS 2020 ANNUAL REPORT (https://www.ocwd.com/wp-content/uploads/2020-gwrs-annual-report-appendices-1.pdf)