## Slide 1: LVMWD 水質予測
熊谷 渉
YHQ MK本部 イノベーションセンター
プロジェクトデザイン部 オペレーショナルエクセレンスGr.
2023年2月7日
米国再生水NAWI

## Slide 2: 熊谷の目的・今回のサマリ
熊谷の目的
今回のサマリ
  LVMWDの水質（透過水の導電率）について、時系列モデルをベースに予測モデルを検討した。
  モデル戦略を少し変えて、複雑なモデリングを適用し、予測のポテンシャルを確認することを優先した。
  下記を示唆する結果を得た。
    定常的かつ細かな挙動：他の変数との関係を踏まえないと難しい
    非定常かつ大域的な挙動（悪化傾向）：追える可能性がある
中長期：NAWI RO膜運転に繋げるための最適化モデル／方法を検討・検証する。
短期：操業データを分析し、ROモデルを検討する。

## Slide 3: 解析方針：細分化された目的
目的を細分化すると、下記の3段階に分けられる。
（3）RO膜劣化も考慮した運転（膜延命）
（1）流入・透過水質を考慮した運転（水質の確保）
（2）RO膜閉塞状態も考慮した運転（膜閉塞状態の監視）
再生水需要をギリギリ満たすように、過度な薬液添加を削減
閉塞度が基準を満たすときに膜を洗浄する、最低限の閉塞防止を実施
（過度な薬液洗浄／閉塞防止剤を削減）
運転を継続し、膜寿命が基準を満たすときに膜を交換（無駄な交換を削減）
（膜劣化が激しい場合はそれをカバーして、延命させるなど）
膜状態固定の最適化
膜状態監視を活かした
最適化
1. RO解析方針

## Slide 4: Focused Region
Expand the control and considered value step by step.
  Fix to the actual value when optimization calculation if the value is not considered
RO
NaClO
UF
Acid
Potable Water
UV / AOP
UV Radiation with H2O2 or NaClO
Anti-Scalant
Water Quality
(1) Considering permeate water quality and feed flow
Degree of Clogging
Membrane Cleaning
Membrane Life
Monitoring membrane status
1. RO解析方針
Given Region
Given Region
Non-Monitoring membrane status
Subject to be optimization target if interchangeable with RO.
(2) Considering clogging status of RO membrane (monitoring the clogging)
(3) Considering deterioration of RO membrane (the life extension)
Notes: Based on the steps, RO analytical policy is to expand the control and considered value step by step. First step is to control and consider yellow values. Green values are added in second step and red values are added in third step as well. But gray regions are considered as given area in RO optimization, so they are fixed to actual value when calculation.

## Slide 5: Objective (1): Operation considering permeate water quality and feed flow
Optimization: Reduce chemical costs within the balance of water quality and flow rate in Pre & Post-RO.
Modeling: Predict Post-RO water quality and flow rate based on Pre-RO data.
Post-RO
Water Quality
Pre-RO
Water Quality and Flow Rate
Time
Time
1. RO解析方針
RO
NaClO
UF
UV / AOP
UV Radiation with
H2O2 or NaClO
Acid
Potable Water
Anti-Scalant
Water Quality
Degree of Clogging
Membrane Cleaning
Membrane life
Flow rate should be constant.
Given Region
Given Region
Predict water quality
Decide operation values
Prediction Model
Optimization Model
Notes: We are trying the first step now. This is an overview in first step. Optimization is to reduce chemical costs ~ Post-RO. And modeling is to predict ~. Please have a look at the lower figure. Left is water quality and flow rate in pre-RO. We plan to predict water quality in post-RO from left data. After that, we plan to decide the best operation values from right data by optimization. So, we need to build the quality prediction model and optimization model. This is the end of RO analytical policy. I’ll switch to Imoto-san.

## Slide 6: LVMWD: Overall view of RO system
3 Stages configuration and Toray’s TM720-370 is deployed
  Data Period: from May 2020 to October 2022 (three years).
  Data Interval: 1 minute or daily.
RO
UF
Potable Water
UV／AOP
measuring point
P
pump
2. LVMWDデータ
Notes: Now, Let’s start with Data Description. First is overall view of the RO membrane system of Las Virgenes.
The RO system of Las Virgenes consists of three stages, 1st, 2nd, 3rd stage from the upstream.
RO membranes are Toray’s TM720-370.
〇×marks are the measuring point. They collect the data like pressure, conductivity, TOC and so on.
〇P indicates the place of pump.
About three years data from 2020 are available. We converted minute data to daily trend.
Through the daily trend, we wanted to see the long-term trend of each variable.

## Slide 7: 透過水 導電率データ
生データ（1min）は外れ値を多く含んでおり、2021年7月以降に限定するしか無さそう。
2. LVMWDデータ
日付の形式をやり直す
1段目 透過 導電率（30min）
1段目 透過 導電率（1min）
前半はほぼ外れ値
前半除去
2段目 透過 導電率（1min）
3段目 透過 導電率（1min）
Combined 透過 導電率（1min）

## Slide 8: データの加工
2. LVMWDデータ
日付の形式をやり直す
下記の手順で、データを加工した。上下限で外れ値を除去してから、ダウンサンプリングすると、外れ値の影響。
1段目 透過 導電率（30min）
1段目 透過 導電率
1day
30min
1段目 透過 導電率（30min）

## Slide 9: LVMWD
目的を細分化すると、下記の3段階に分けられる。
3. モデリング戦略

## Slide 10: LVMWD
目的を細分化すると、下記の3段階に分けられる。
4. 予測結果

## Slide 11: 導電率：有効なデータ範囲・種類
2021年7月以降で、外れ値の影響が少ない30minが良さそう。
1段目 透過 導電率（30min）
1. 今後のタスク
1段目 透過 導電率
1day
30min

## Slide 12: 導電率：外れ値除去⇒移動平均
1段 透過 導電率
1. 今後のタスク
30min、2021-07~2022-09
データ数を極端に減らさずに、挙動が見えやすくなった。
生
加工
単位のmu：接頭辞μ(10-6)
RO流入 導電率
2段 透過 導電率
3段 透過 導電率
窓幅：96step（2日間）
下限：250、上限：2000
下限：7、上限：40
下限：5、上限：45
下限：10、上限：50

## Slide 13: 導電率(1day/30min)：外れ値除去⇒移動平均
1段 透過 導電率
1. 今後のタスク
2021-07~2022-09
1dayは外れ値に影響を受け、挙動が異なる期間がある。
1day
30min
単位のmu：接頭辞μ(10-6)
RO流入 導電率
2段 透過 導電率
3段 透過 導電率
1day窓幅：5step（5日間）
30min窓幅： 96step（2日間）

## Slide 14: 2月上旬までの解析方針
2月上旬までは下記の方針で解析を進める
目的1：30minデータで、日々の導電率変動をモデル化する
  変数間の関係を見る
  井本さん
目的2：30minデータで、数か月単位の導電率悪化をモデル化する
  自己回帰成分との関係を見る
  膜の詰まりが要因なので、予測できない差分は物理モデルの知見で改善していくが、ファーストステップとして実施
  熊谷
1. 今後のタスク

## Slide 16: RO膜の性能
・・・
濃縮水（排水）
供給水
透過水
濃度
体積流量
導電率
回収率[%]＝
LRV＝
対数減少値（ウイルス除去率）
イオン状物質除去率
除去率
RO膜の性能
RO膜性能は、除去率と回収率で測られている。
膜性能を評価するには、どのデータを監視する必要があるか？

## Slide 17: 解析まとめ
2. 今後のタスク
全TagリストとP&IDをもとに、受領済のプラント情報を正確に把握する。
熊谷・(川田)
担当
井本
川田
次回問合せの準備をしておく
タスク
RO膜周辺の単体データについても、トレンド図を作成する。
透過圧力・流量含む
ただし、流量は温度補正の可能性があるため、東レシートから確認
一部のデータに限定して、分析する。
井本
洗浄未発生の期間に限定（ただし、複数の期間で試す方が良い）
透過水質は「透過導電率の悪化」に注目
（水温などの外乱について網羅的に関係を確認）