## Slide 1: NAWI RO Analysis Progress Report
W. Kumagai, H. Soya, R. Imoto
Operational Excellence Gr., Project Design Dev.,
Innovation Center, MKHQ, YHQ
August 30th, 2023
SGDC

## Slide 2: Agenda
RO Operation Optimization
RO Permeate Water Quality Prediction / Q&A
RO Optimization Simulation / Q&A
RO Membrane Scaling Modeling / Q&A
9:05 – 9:10
9:10 – 9:35
9:35 – 10:00
10:00 – 10:30
Notes: This is today’s agenda. There are four parts, first part is RO Operation Optimization and Concept, second is RO Permeate Water Quality Prediction, third is Optimization Simulation, fourth is RO Membrane Scaling Modeling. We’ll have Q&A part at the end of second, third, fourth parts. If you have any questions, please save them until Q&A part.

## Slide 3: Objective of RO Optimization
Chemical dosing costs are minimized considering RO membrane condition within the range of maintaining water quality and flow rate.
  Maintaining high recovery rate, good water quality (high salt rejection), and extending RO membrane life.
  Considering water quality, permeate flow rate, and RO clogging status.
RO
NaClO
UF
Sulfuric Acid／Anti-Scalant
Potable Water
UV / AOP
UV Radiation with H2O2 or NaClO
Water quality
Degree of Clogging
Membrane cleaning
Membrane life
1. RO Operation Optimization
Given Region
Given Region
Subject to be optimization target if interchangeable with RO.
Chemical costs
Chemical costs
Water quality and flow rate to be maintained
Clogging due to fouling Scaling by crystallization Bio-fouling by deposit
Notes: First, I explain RO Operation Optimization. This shows potable water reuse process. Water from sewage plant is treated by this process and supplied to potable reuse. It mainly consists of UF, RO, UV, and AOP process units. The objective of RO optimization shows chemical dosing costs are ~. There are chemical costs in many places, for example, total chlorine, Sulfuric Acid, and anti-scalant. Moreover, there are considering conditions in many places, for example, recover rate, water quality, and RO clogging status. RO clogging is called bio-fouling or scaling. RO analytical policy is to expand the control and considered value step by step. First stage is to control and consider water quality and clogging.

## Slide 4
3 Stages configuration.
Water quality data is RO permeate TOC and Conductivity.
  Monitoring LRV (logarithmic reduce value) as water-quality standards.
1. RO Operation Optimization
Overall view of LVMWD RO system
RO system
measuring point
P
pump
Water Quality Targets are shown in red.
Notes: This shows Las Virgenes RO system. This is 3 stages configuration. Water quality data is RO permeate TOC and Conductivity. They are measured at each RO stage permeate point. Water-quality standards is monitored as LRV.

## Slide 5: Plant Scheduling Optimization
RO optimization problem is formulated into a scheduling optimization.
The procedure consists of the following steps.
3. RO Optimization Simulation > Simulator
A
B
C
Facility Model
: Optimization Variable
1. Drawing Flow Chart
(Operational Cost)
(Facility Characteristics)
2. Formulation
Optimization Problem
Time
Operational Cost is $XX.
3. Calculation
Operational Schedule
Sample Flow Chart
Notes: RO optimization problem~. The procedure~. First step is drawing flow chart. In this chart, arrows connecting objects are assigned optimization variables. The object plays the role of exogenous variable, mathematical model, and predictive variable. Second step is formulation optimization problem. I define the minimizing the objective function and the constraints. Third step is calculation operational schedule. I solve the formulated problem using optimization algorithm.

## Slide 6: Functional Configuration of RO Optimization Simulator
3. RO Optimization Simulation > Simulator
Unify the file format, e.g., add calculated tag and up/down resampling according to given timespan based on master data.
Generate optimization / prediction model files with user-specified modeling and parameter files using data in the training / optimization period.
Calculate prediction model error by input optimization variables fixed to actual value into optimization model, i.e., predict validation.
Solve the RO plant scheduling problem by optimizer.
Calculate each average value and LRV of water quality, and draw each variable trend chart including LRV.
Pre-processing
Generate Model and Params
Model Validation
Optimize
Post-processing
Notes: This shows functional configuration of RO optimization simulator. Step1 is data preprocessing. Step2 generates model and parameters including prediction model files. Step3 is model validation. this calculates prediction model error by input~. Step4 solves the RO plant~. Step5 calculates each~.

## Slide 7: Flow Chart for RO Optimization
3. RO Optimization Simulation > Problem Formulation
We define the flow chart, variables, mathematical models.
  The model dose not yet include RO Membrane Scaling / Fouling model.
RO Whole Part
RO Each Stage Part
Exogenous Variable
Predictive Variable
(water quality)
Mathematical Model
(prediction model)
Notes: This is the flow chart for Las Virgenes model. I divided into the RO whole part and RO each stage part. The storage, the square, and hexagon object are exogenous, predictive variable that is water quality, and mathematical model including prediction model based on multi regression model. The arrow toward the object is input variable and the arrow from the object is output variable. But the model dose not yet include RO membrane scaling or fouling model.

## Slide 8: Optimization Problem
3. RO Optimization Simulation > Problem Formulation
Objective Function
Main Constraint Conditions
Water Quality Standards and Upper / Lower limit
Logarithmic Reduction Value (LRV):
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Combined Permeate EC |  | 0 | 50
Combined Permeate TOC |  | 0 | 0.15
Combined EC LRV | - | 1.5 | 2.0
Combined TOC LRV | - | 1.5 | 2.2
Description | Units | Lower | Upper
Stage 1 Permeate EC |  | 0 | 50
Stage 2 Permeate EC |  | 0 | 50
Stage 3 Permeate EC |  | 0 | 60
Combined Permeate EC |  | 0 | 50
Combined Permeate TOC |  | 0 | 0.15
Combined EC LRV | - | 1.5 | 2.0
Combined TOC LRV | - | 1.5 | 2.2
are calculated by the prediction model at the previous part.
UF Filtrate Total Chlorine
Minimizing chemical cost while satisfying water quality standards.
Total Steps
Unit Cost
Notes: In this case, the optimization problem is minimizing the chemical dosing cost while satisfying water quality standards. The objective function f is formulated as the sum of the UF filtrate total chlorine of the optimization period. The main constraint conditions is water quality standards and upper or lower limit. This table shows each upper and lower limit about permeate EC and TOC. Especially, the EC LRV’s range is from 1.5 to 2.0, and TOC LRV’s range is from 1.5 to 2.2 in Las Virgenes plant. Moreover, the permeate quality values are calculated by the prediction model at the previous part.

## Slide 9: Permeate Water Quality
The prediction performance for global trends is good.
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
3. RO Optimization Simulation > Prediction Result
Blue: Actual / Orange: Prediction
Actual Ave.: 0.067 [mg/L],
Predict Ave.: 0.064 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Predict Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Predict Ave.: 2.03
Actual Ave.: 1.83,
Predict Ave.: 1.83
Training Period: from March 7th to 14th, 2022 (1week)
Optimization Period : from March 14th to 21th, 2022 (1week)
Data Interval: 1hour
*The results are NOT optimized when input data is fixed to actual data.
Notes: Next, I talk about prediction and optimization results. This shows prediction results by simulator. Scheduling period is 1week and data interval is 1hour. left figure is combined permeate TOC and right figure is combined permeate Conductivity. Lower figures are LRV of TOC and EC. Blue line is actual data and Orange line is prediction data. Comparing average value between actual and prediction, the error is small. So, the prediction performance for global trends is good.

## Slide 10: Search Solution Transition
After getting a feasible solution, the solution is improving .
3. RO Optimization Simulation > Optimization Results
*Total calculation time is about 10 minutes.
(Generations)
Objective Function Value
Constraint Violation
Get feasible solution
Best Solution Transition
Population size: 100
Notes: This shows best solution transition trend during optimization. x-axis is loop or iteration times and y-axis is solution value. Blue line is objective function value f and orange line is constraint violation v. This point is to get feasible solution. After that, the solution is improving f. Total calculation time is about 10minutes in this laptop PC.

## Slide 11: Chemical and Exogeneous Variables
UF Total Chlorine [mg/L] (Chemical Dosing Cost)
S1 Feed Pressure [psi] (Fixed)
S1 Feed Flow [gpm] (Fixed)
S1 Feed EC [uS/cm] (Fixed)
Feed TOC [mg/L] (Fixed)
3. RO Optimization Simulation > Optimization Results
The schedule shows reducing chemical costs comparing to actual data.
Blue: Actual / Orange: Optimized
Actual Ave.: 0.40 [mg/L],
Optimized Ave.: 0.38 [mg/L]
Notes: This shows optimized schedule. Left figure is UF filtrate total chlorine, right figures are exogeneous variable. Comparing average value between actual and optimized, optimized schedule is slightly lower than actual data. It means to reduce chemical costs.

## Slide 12: Water Quality Variable
Actual Ave.: 0.067 [mg/L],
Optimized Ave.: 0.063 [mg/L]
Actual Ave.: 20.76 [uS/cm],
Optimized Ave.: 20.87 [uS/cm]
Actual Ave.: 2.01,
Optimized Ave.: 2.03
Actual Ave.: 1.83,
Optimized Ave.: 1.83
There is a slight change but meeting the WQ standards of LRV.
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [mg/L]
3. RO Optimization Simulation > Optimization Results
Notes: This shows water quality variable. There is a slight change comparing actual and optimized value. But~ by optimization.

## Slide 13: Optimization Effect Calculation
There is a little improvement in the period and condition.
  This model does NOT yet RO membrane fouling model.
3. RO Optimization Simulation > Optimization Effect
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err.
Total Chlorine [mg/L] | 0.40 | 0.38 | - 0.02 |  | - 0.02
Conductivity [uS/cm] | 20.76 | 20.87 | + 0.11 | + 0.11 | - 0.0004
TOC [mg/L] | 0.067 | 0.063 | - 0.004 | - 0.004 | + 0.0004
LRV Conductivity | 1.83 | 1.82 | - 0.01 | - 0.01 | + 0.002
LRV TOC | 2.01 | 2.03 | + 0.02 | + 0.02 | + 0.003
Notes: This is optimization effect. They are water quality’s difference between actual and optimized value. Moreover, removing the effects prediction model error from this value is very small. So, it is considered there is a little improvement in the period and condition. But this model does not yet~.

## Slide 14: Future Tasks
To introduce Random Forest into optimization.
  Metaheuristic algorithm calls RF 500,000 times
  It needs the way to reduce the calculation time.
To introduce RO membrane Fouling model and determine chemical cost considering RO Fouling.
3. RO Optimization Simulation > Optimization Effect
Notes: Future task is to introduce random~.

## Slide 15: 透過水質
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
2. OCWD > 5weeks 予測結果
Blue: Actual / Orange: Prediction
Optimized Period: from May 20th to June 24th, 2022
1w学習＆1w最適化を逐次シフトさせていく
1,2,5週目はEC予測精度が悪い
3,5週目はTOC予測精度が悪い

## Slide 16: 説明変数の影響
2. OCWD > 5weeks 予測結果
Blue: Actual / Orange: Prediction
1,2週目はFeed ECが傾向違う？
3週目はInhibitorが傾向違う

## Slide 17: 操作計画：コスト変数
Sulfuric Acid [ton/hour]（コスト）
2. OCWD > 5weeks 最適化結果
Blue: Actual / Orange: Optimized
Inhibitor [ton/hour]（コスト）
4週目は下限に張り付く

## Slide 18: 操作計画：透過水質
2. OCWD > 5weeks 最適化結果
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
1,2,3,5週目はLRV上限に張り付く

## Slide 20: [LVMWD] RO System Configuration and Measurement Points
P
・Feed Free Chlorine
・Feed Conductivity
・Feed pH, TOC, Temp
・Feed Pressure
・Feed Flow (Calc)
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Permeate Flow
・Permeate Conductivity
・Combined Permeate TOC
・Combined Permeate Conductivity
・Concentrate Pressure
・Concentrate Flow
・Inlet Free Chlorine
・Inlet Total Chlorine
・Inlet pH
・Inlet UVT
・Inlet Flow
UV
・Outlet Free Chlorine
・Outlet Total Chlorine
・Inlet UVT
・UV Dose
・UV Intensity
・UV Lamp Power (Constant 50%)
RO 1st Stage
RO 2nd Stage
RO 3rd Stage
Feed Pressure
Concentrate Pressure
Feed Pressure
P
This pump decides the feed flow to RO.
a
b
c
d
e
<Differential Pressure>
Stage 1 = －
Stage 2 = －
Stage 3 = －
a
b
b
c
d
e

## Slide 21: Introduction：summary up to the previous meeting
      Data Preprocessing
        creating “master data“ for analysis from raw dataset by pretreatment including Data Cleaning and/or Filtering
      Overview of the water quality prediction model
        Focused Period
          Focusing on the period while all variables are available and operational situation with RO membrane is stable.
        Target Variables
          Treated water is required to satisfy the standard indicated permeate conductivity and permeate combined TOC. We focused on each stage permeate conductivity（Targe①～③）and permeate combined TOC（Target④）.
      Continuous Chain Evaluation（1 week Training and 1 week Prediction）
        “Prediction trend” is totally compiled with each weekly prediction trend all through the period.
2. RO Permeate Water Quality Prediction

## Slide 22
Model：Multiple Regression Model ＆ Radom Forest
Used Variables：
Target number Variable Name | Target① Stage1 Permeate EC | Target② Stage2 Permeate EC | Target③ Stage3 Permeate EC | Target④ Permeate TOC
RO Stage 1 Feed Pressure | X |  |  | X
RO Feed EC | X |  |  | X
RO Feed Flow* | X |  |  | X
RO Feed Temperature | X | X | X | X
RO Feed pH | X |  |  | X
UF Filtrate Total Chlorine | X | X | X | X
RO Stage 2 Feed EC* |  | X |  | 
RO Stage 2 Feed Flow* |  | X |  | 
RO Stage 3 Feed Pressure |  |  | X | X
RO Stage 3 Feed EC* |  |  | X | 
RO Stage 3 Feed Flow* |  |  | X | 
RO Feed TOC |  |  |  | X
Water Quality Model Details
※Conductivity = EC *Calculation Tag
Water Quality Model
Output
Input
X
2. RO Permeate Water Quality Prediction

## Slide 23: Data Preprocessing
  Step1 : Data Cleaning Getting rid of the data during the period when it is as following: ① First Feed Flow Rate equal 0, ② The measurement value remains same value for more than 10 mints, ③ Changing rate of measurement value is more than 20% ( / mint) and etc.
2. RO Permeate Water Quality Prediction
Feed Flow Rate Raw Data
Zoom up
①
②
③
  Step2 : Filtering This step (ⅰ or ⅱ) is applied only when step1 pretreatment does not have enough efficacy.
    Analysis of Variance（Removing the outlier which is beyond 3σ.）
    Kalman Filter is applied.
DATE
DATE
DATE
y=0
More than 10 min
Changing rate
More than 20%
Y
Y
Y

## Slide 24: Overview of the water quality prediction model
2. RO Permeate Water Quality Prediction
RO system
measuring point
P
pump
Target①
Target②
Target③
Target④
RO Permeate Water Quality Prediction targets are Target①~④
  Focused Period: July 1st, 2021 ~ July 27th, 2022
    all variables are available and operational situation with RO membrane is stable.
  Target Variables: 1st to 3rd stage permeate conductivity and combined TOC
    Treated water is required to satisfy the standard indicated permeate conductivity and TOC.

## Slide 25
Index | Stage2 Permeate EC
RMSE | 2.46* (uS/cm)
MAPE | 5.59* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ② Stage2 Permeate EC ～

## Slide 26
Index | Stage3 Permeate EC
RMSE | 2.30* (uS/cm)
MAPE | 4.70* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Multiple Linear Regression
A-1：Prediction results from systematically pre-processed data
～ Target ③ Stage3 Permeate EC ～

## Slide 27
Index | Stage2 Permeate EC
RMSE | 1.40* (uS/cm)
MAPE | 4.37* (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ② Stage2 Permeate EC ～

## Slide 28
Index | Stage3 Permeate EC
RMSE | 2.02 (uS/cm)
MAPE | 4.06 (%)
Pre-processed actual data
Predicted data
2. RO Permeate Water Quality Prediction > Results by Random Forest
B-1：Prediction results from systematically pre-processed data
～ Target ③ Stage3 Permeate EC ～

## Slide 29: Module Configuration
3. RO Optimization Simulation > Simulator
main.py
Optimization Module
Optimization Problem
model
Input data
Definition objective and constraint functions.py
import_model.py
1st permeate EC Prediction module
Defined Optimization Problem
Defined Optimization Solver
Automatically created model files by training
pkg
config.ini
2nd permeate EC Prediction module
Execute each function
…

## Slide 30: Variable List
LVMWD
ID No. | Description | Units | Opt. Variable / Fixed Parameter
ID0000 | UF Filtrate Total Chlorine | ton/day | Optimization Variable
ID0001 | Feed EC |  | Fixed Parameter
ID0002 | Feed TOC | mg/L | Fixed Parameter
ID0003 | Feed Temperature |  | Fixed Parameter
ID0004 | Feed pH | - | Fixed Parameter
ID0100 | Stage 1 Feed Pressure | psi | Fixed Parameter
ID0101 | Stage 1 Feed Flow Rate | gpm | Fixed Parameter
ID0102 | Stage 1 Permeate Flow Rate | gpm | Fixed Parameter
ID0200 | Stage 2 Feed Flow Rate | gpm | Fixed Parameter
ID0201 | Stage 2 Permeate Flow Rate | gpm | Fixed Parameter
ID0300 | Stage 3 Feed Pressure | psi | Fixed Parameter
ID0301 | Stage 3 Feed Flow Rate | gpm | Fixed Parameter
ID1000 | Stage 1 Permeate EC |  | Intermediate Variable
ID2000 | Stage 2 Feed EC |  | Intermediate Variable
ID2001 | Stage 2 Permeate EC |  | Intermediate Variable
ID3000 | Stage 3 Feed EC |  | Intermediate Variable
ID3001 | Stage 3 Permeate EC |  | Intermediate Variable
ID4000 | Permeate EC |  | Intermediate Variable
ID4001 | Permeate TOC | mg/L | Intermediate Variable
ID No. | Description | Units | Opt. Variable / Fixed Parameter
ID0000 | UF Filtrate Total Chlorine | ton/day | Optimization Variable
ID0001 | Feed EC |  | Fixed Parameter
ID0002 | Feed TOC | mg/L | Fixed Parameter
ID0003 | Feed Temperature |  | Fixed Parameter
ID0004 | Feed pH | - | Fixed Parameter
ID0100 | Stage 1 Feed Pressure | psi | Fixed Parameter
ID0101 | Stage 1 Feed Flow Rate | gpm | Fixed Parameter
ID0102 | Stage 1 Permeate Flow Rate | gpm | Fixed Parameter
ID0200 | Stage 2 Feed Flow Rate | gpm | Fixed Parameter
ID0201 | Stage 2 Permeate Flow Rate | gpm | Fixed Parameter
ID0300 | Stage 3 Feed Pressure | psi | Fixed Parameter
ID0301 | Stage 3 Feed Flow Rate | gpm | Fixed Parameter
ID1000 | Stage 1 Permeate EC |  | Intermediate Variable
ID2000 | Stage 2 Feed EC |  | Intermediate Variable
ID2001 | Stage 2 Permeate EC |  | Intermediate Variable
ID3000 | Stage 3 Feed EC |  | Intermediate Variable
ID3001 | Stage 3 Permeate EC |  | Intermediate Variable
ID4000 | Permeate EC |  | Intermediate Variable
ID4001 | Permeate TOC | mg/L | Intermediate Variable

## Slide 31: 透過水質
トレンドを大まかに捉えているが、ECの予測値が実績よりも若干低い。
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
2.2 OCWD > 1st week 予測結果
Blue: Actual / Orange: Prediction
Actual Ave.: 0.055 [ppm],
Predict Ave.: 0.052 [ppm]
Actual Ave.: 23.48 [uS/cm],
Predict Ave.: 18.61 [uS/cm]
Actual Ave.: 2.22,
Predict Ave.: 2.24
Actual Ave.: 1.88,
Predict Ave.: 1.99

## Slide 32: 探索結果（最良解の推移）
実行可能解を得て、コストを改善する解が得られている。
2.2 OCWD > 1st week 最適化結果
10,000の半分で止めた
Blue: Objective Function Value /
Orange: Constraint Violation
約9分

## Slide 33: 操作計画：コスト変数と固定変数
Sulfuric Acid [ton/hour]（コスト）
S1流入圧力 [psi]（固定）
S1流入量 [gpm]（固定）
S1流入EC [uS/cm]（固定）
流入TOC [ppm]（固定）
Inhibitor [ton/hour] （コスト）
2.2 OCWD > 1st week 最適化結果
LRV基準の制約によって、Inhibitorが実績とほぼ同じ値になっている。
Blue: Actual / Orange: Optimized
Actual Ave.: 0.39 [ton/hour],
Optimized Ave.: 0.38 [ton/hour]
Actual Ave.: 0.0559 [ton/hour],
Optimized Ave.: 0.0560 [ton/hour]

## Slide 34: 操作計画：透過水質
ECのLRV基準の上限に位置する解となっている。
2.2 OCWD > 1st week 最適化結果
Blue: Actual / Orange: Optimized
Combined Permeate EC [uS/cm]
Combined Permeate TOC [ppm]
Actual Ave.: 0.055 [ppm],
Optimized Ave.: 0.053 [ppm]
Actual Ave.: 23.5 [uS/cm],
Optimized Ave.: 18.7 [uS/cm]
Actual Ave.: 2.22,
Optimized Ave.: 2.23
Actual Ave.: 1.88,
Optimized Ave.: 1.98

## Slide 35: コスト換算
約47$/day(18K$/year, 2.5M\/year)の削減効果と見積もれる。
  ただし、この条件では、ほぼ改善の余地が無いと見積もれる。
2.2 OCWD > 1st week 最適化結果
Variable | Actual Ave. | Optimized Ave. | Diff (Opt – Act) | Model Error | Diff – Err. | Cost [$/day]
Acid [ton/hour] | 0.39 | 0.38 | - 0.009 |  | - 0.009 | - 53.3
Inhibitor [ton/hour] | 0.0559 | 0.0560 | + 0.0001 |  | + 0.0001 | + 6.22
EC [uS/cm] | 23.5 | 18.7 | - 4.74 | - 4.87 | + 0.13 | 
TOC [mg/L] | 0.055 | 0.053 | - 0.002 | - 0.003 | + 0.001 | 
LRV EC | 1.88 | 1.98 | + 0.30 | - 0.01 | - 0.003 | 
LRV TOC | 2.217 | 2.234 | + 0.02 | + 0.02 | - 0.005 | 
Total |  |  |  |  |  | - 47.1