## Slide 1: Cost Calculation for UF Optimization

## Slide 2: Optimization Scenario 1: Given Fixed Flux and Period
Input from user:
  Fixed Flux
  Period (Default 30 days)
Objectives:
  Minimize Total cost of operation
  (Energy cost for pumping the water during production + Pumping cost for (BW+MC+RC) + Chemical cost for MC and RC)
  Minimize membrane life span loss due to chemical exposure
  Meet recovery rate
Assumption/ Constraints:
  Membrane parameters (Area, maximum allowable TMP)
  Operation parameters
      Fixed duration for MC, BW and RC
      Constant water consumption for MC, BW and RC
      Hypo Chemical dosage range for MC (300 to 1100 ppm)
      Chemical cleaning (MC) interval(>2 days,<7 days)
      Permeability loss between 2 RCs <X% (0.02 gfd/psi)
      Recovery rate> 95%
      TMP can be used calculate pump head during production
      Pump Efficiency curve will be used to calculate Electrical energy consumption
      Constant pump flow and head during BW, MC and RC
Output/Decision variables:
  Optimum number of MCs
  Optimum MC intervals (Dates of recommended MC)
  Optimum MCs dosage (Chemical Conc in each MC)

## Slide 3: Cost Calculation
5 Cost components are considered for cost Calculation:
Cost of pumping feed water thru the membrane during the production modes
Cost of pumping the chemical solution thru the membrane during MCs
Sum of Chemical cost in all MCs
4. Cost for pumping the chemical solution thru the membrane during RC at the end of 30 days period
(This cost is Constant Always & hence can be ignored)
5. Chemical cost in RC (Since chemical concentrations are not varied in RC, This cost is Constant Always & hence
can be ignored)
Total cost is sum of above 5 cost components (4 & 5 can be ignored as they are constant)

## Slide 4: Cost of pumping feed water thru the membrane during the production modes
Step 1: Predict TMP in all production modes based on SAO models
Step 2: Estimate Predicted Feed Pressure in all production modes from predicted TMP
Predicted Feed Pressure = Predicted TMP + Avg. Filtrate Press (~1.5) + Height difference (~3.7)
MAPE = 4.87%
Step 3: Calculate feed water Pump discharge flowrate, flux*membrane area
Step 4: Estimate Pump Output power at each timestamp in kW, Pout = flowrate*predicted pressure

## Slide 5: Cost of pumping feed water thru the membrane during the production modes
Step 5: Integrate Pump Output power (Pout) at each timestamp to obtain total output power in kWh
Step 6: Obtain total input power to Pump in KWh Pin_Total=Total output power/Efficiency(0.6)
Step 7: Estimate the total pumping cost, Total input power (KWh)* ($/KWh) cost of electricity per kWh
Cost of electricity is assumed to be constant $0.14/kWh

## Slide 6: Cost of pumping the chemical solution thru the membrane during MCs
Assumptions:
Constant flow (110 gallon/MC) and Constant discharge Pressure (10m of water) for all MC
Total power consumption in each MC, (in kWh) = (Total flow*Pressure)/Efficiency(0.6)
Pumping cost in all MCs = No. of MCs X Total power consumption in each MC (in kWh) X ($/kWh) power cost

## Slide 7: Cost of Chemical in MC
Assumptions:
Only cleaning with Hypochlorite is considered in MC
MC Hypo (NaOCl) Conc | Amount of 12.5% NaOCl solution required (gal) | Cost of NaOCl solution ($/gal) | Chemical Cost ($)
300 ppm | 0.24 | 3 | 0.72
500 ppm | 0.4 | 3 | 1.2
700 ppm | 0.56 | 3 | 1.68
900 ppm | 0.72 | 3 | 2.16
1100 ppm | 0.88 | 3 | 2.64
1200 ppm | 0.96 | 3 | 2.88
1500 ppm | 1.2 | 3 | 3.6
2000 ppm | 1.6 | 3 | 4.8

## Slide 8: UF Process Optimization: Minimization of Total cost

## Slide 9: Constraint on Permeability loss
Assumptions:
Less than 10% permeability loss (measured after a recovery clean) in the first year of operation
Less than 30% permeability loss (measured after a recovery clean) over 10 years of operation
Maximum permeability observed for UF2 is 10.8 gfd/psi at 20°C.
Therefore, after a recovery clean, UF2 permeability should remain above 9.72 gfd/psi =(10.8 -10% of 10.8) at 20°C for the first year of operation.
After 10 years, the permeability after a recovery clean should be higher than 7.56 gfd/psi = (10.8-30%of 10.8) at 20°C for UF2 .
0.24 gfd/psi =(9.72-7.56)/9 is the maximum allowable loss per year for year 2 to 10
0.02 gfd/psi = (0.24/12) is the maximum allowable loss per month for year 2 to 10

## Slide 10: Constraint on Chemical (Hypo) Load on Membrane during MC & RC
Assumptions:
Maximum allowable chemical load of Hypo on UF2 membrane is 1,000,000 ppm*hr for 10 years of operation
Maximum allowable chemical load of Hypo on UF2 membrane is 100,000 ppm*hr =(100,000/10) per year
Maximum allowable chemical load of Hypo on UF2 membrane is 8,333.34 ppm*hr =(10,000/12) per month
Typically, One RC is done with 2,000 ppm Hypo per month for 3 hr duration, (2,000*3)=6,000 ppm*hr
Hence, maximum allowable MC chemical load for Hypo is (8,333.34-6,000)=2,333.34 ppm*hr per month

## Slide 11: Optimized Operation for 25 GFD flux with Permeability loss<0.02gfd/psi, MCChemLoad<2333ppm*h (GA Iteration=500)
Estimated Cost for Actual Op ($) | Estimated Cost for recommended Optimized op ($)
USD 26.83 (5 MCs – 500 ppm) | USD 23.01 (5 MC -300 ppm)
Overall Permeability drop (1.854 GFD/psi) Increase in TMP (-1.541 psi) | Overall Permeability drop (1.669 GFD/psi) Increase in TMP (0.599 psi)
Cost per M3 water: 0.01605 USD/M3 | Cost Per M3 Water: 0.01469 USD/M3
8.5% Reduction in Operation cost
Actual, Operation with 25 gfd flux involving 4 MCs in ~33 days at ~7 days interval with 500 ppm Hypo is bit away from the optimal operation. Hence, more than 12% reduction in cost can be achieved through optimization

## Slide 12: Optimized Operation for 25 GFD flux with Permeability loss<0.02gfd/psi, MCChemLoad<2333ppm*h (GA Iteration=300)
Estimated Cost for Actual Op ($) | Estimated Cost for recommended Optimized op ($)
USD 22.40 (4 MCs – 500 ppm) | USD 20.91 (4 MC:3MCs-300 ppm, 1MC-500 ppm)
Overall Permeability drop (0.5880 GFD/psi) Increase in TMP (0.0001 psi) | Overall Permeability drop (0.3935 GFD/psi) Increase in TMP (0.03986 psi)
Cost per M3 water: 0.01563 USD/M3 | Cost Per M3 Water: 0.01461 USD/M3
6.52% Reduction in Operation cost
Actual, Operation with 25 gfd flux involving 4 MCs in ~33 days at ~7 days interval with 500 ppm Hypo is very close to the optimal operation (4Mcs, 3 with 300 & 1 with 500 ppm at ~7days interval). Hence, reduction in cost achieved through optimization is less than 7%

## Slide 13: Optimized Operation for 44.93 GFD flux with Permeability loss<0.02gfd/psi, MCChemLoad<2333ppm*h, 12% reduction in production cost/m3 (Terminated after GA Iterations = 62)
Estimated Cost for Actual Op ($) | Estimated Cost for recommended Optimized Op ($)
USD 39.10 (7 MCs – 500 ppm) | USD 34.12 (5 MC -300 ppm)
Overall Permeability drop (3.774 GFD/psi) Increase in TMP (3.829 psi) | Overall Permeability drop (2.298 GFD/psi) Increase in TMP (1.432 psi)
Cost per M3 water: 0.01764 USD/M3 | Cost Per M3 Water: 0.01539 USD/M3
12.75% Reduction in Operation cost
Actual, Operation with 45 gfd flux involving 7 MCs in 27.5 days at ~3.5 days interval with 500 ppm Hypo is away from the optimal operation (5 MCs all 300 ppm at an interval of ~4.5 days). Hence, more than 12% reduction in cost can be achieved through optimization

## Slide 14: Optimized Operation for 44.93 GFD flux with Permeability loss<0.02gfd/psi, MCChemLoad<2333ppm*h, 12% reduction in production cost/m3 not achieved even after GA Iterations = 3000
Estimated Cost for Actual Op ($) | Estimated Cost for recommended Optimized Op ($)
USD 37.54 (6 MCs @~4days interval– 500 ppm) | USD 35.44 (8 MC -300 ppm)
Overall Permeability drop (3.31 GFD/psi) Increase in TMP (2.22 psi) | Overall Permeability drop (2.73 GFD/psi) Increase in TMP (1.56 psi)
Cost per M3 water: 0.01631 USD/M3 | Cost Per M3 Water: 0.01546 USD/M3
5.21% Reduction in Operation cost
Actual, Operation with ~45 gfd flux involving 6 MCs in 28.5 days at ~4 days interval with 500 ppm Hypo is close to the optimal operation (8 MCs 300 ppm at an interval of ~3 days). Hence, reduction in cost achieved through optimization is less than 6%

## Slide 15: UF Optimization @ 45 GFD flux – Permeability Plot
Actual Vs Optimized
Actual Operation
7X 500 PPM MC
1X 500 + 3X 300 PPM MC

## Slide 16: UF Optimization Effect
Estimated Cost for Actual Operation
500 ppm x 7 - Maintenance Cleaning
UF Operations Cost: MC Hypo + Power + Production $39.1
Power Consumption Indices Overall Permeability drop : 3.8 GFD/psi Increase in TMP : 3.8 psi
Cost per m3 and kgal 0.018 $/m3 and 0.068 $/kgal
Estimated Cost for Optimized Operation
500 ppm x 1 + 300 ppm X 3 - Maintenance Cleaning
UF Operations Cost: MC Hypo + Power + Production $33.9
Power Consumption Indices Overall Permeability drop: 2.8 GFD/psi Increase in TMP : 2.0 psi
Cost per m3 and kgal 0.015 $/m3 and 0.057 $/kgal
13% Reduction in chemical & power costs

## Slide 17: Input Parameters for Optimization

## Slide 18: Input parameters required for Optimization
Parameters | Values
Event Data of last RC/MC Event | To be read from online
Membrane Area (ft^2) | 538
Volume of water consumed per BW (Backwash Volume in gallon) | 9.5
Volume of water consumed per MC (Maintenance Cleaning Volume in gallon) | 50
Volume of water consumed per RC (Recovery Cleaning Volume in gallon) | 150
Time duration of each production in between BW (min) | 20
Time duration per Backwash (BW Duration in min) | 2
Time duration per MC (MC Duration in min) | 40
Time duration per RC (RC Duration in min) | 180
Hypochlorite chemical concentrations available for MC (ppm) | [300, 500, 700, 900, 1100]
Hypochlorite chemical concentrations available for RC (ppm) | [2000]
Citric acid chemical concentrations available for RC (ppm) | [2000]
Maximum and Minimum time interval between 2 MCs (in days) | Max 7 days & Min 2 days
Constant operating flux for optimization (gfd) | 40
Total time duration for optimization (Time horizon for optimization) in days | 30
Minimum achievable recovery rate (%), Recovery rate must be more than this value | 95
Maximum allowable permeability loss after the time duration of optimization, Loss in permeability must be less than this value (in gfd/psi) | 0.02
Target number of MCs during the optimization time horizon | 6
Population size in GA | 50
Number of Iteration in GA | 100

## Slide 19
Parameters | Values
Average Filtrate side pressure (psig) | 1.49
Height difference between feed & filtrate side pressure transmitters (psi) | 3.7
Membrane Feed Pump Efficiency | 0.6 (60%)
Cost of electricity (USD/kWh) | 0.14
Average discharge pressure of CIP pump (psig) | 22.5
CIP pump Efficiency | 0.6
Volume of std Hypo solution required per ppm (gallon) | 0.0008
Cost of std Hypo solution (USD/gallon) | 3