## Slide 1: Figure 1.1: Scheduling Problem
A
B
C
Facility Model
Time
Operational Cost is $XX.
(Operational Cost)
(Facility Characteristics)
: Optimization Variable
1. Drawing Flow Chart
2. Formulation
Optimization Problem
3. Calculation
Operational Schedule

## Slide 2: Work001 (OCWD) ：フロー図 (RO Total)
S1_EC
Sulfuric Acid Dosing
ID000
S1_EC
ID001
ID002
コスト元
S1 Feed EC
S1 Feed TOC
透過TOC予測
TOC
RO Feed
scailng予測
scaling
ID003
S1 Feed Pre
ID200
S2 Perm Flow
RO Total
RO Stage1
ID004
UF Filtrate Total Chlorine
RO Stage2
RO Stage3
ID301
S3 Conc Pre
ID100
S1 Perm Flow
ID302
S3 Conc Flow
ID300
S3 Perm Flow
ID1000
ID1001
ID1002
ID003
S1 Feed Flow
S1_Flow
ID1000
ID003
S1 Feed pH

## Slide 3: Work001 (OCWD) ：フロー図 (RO Stage1, 2, 3)
S1_EC
Sulfuric Acid Dosing
ID000
S1_EC
ID001
ID002
コスト元
S1 Feed EC
S1 Feed TOC
RO Feed
ID003
S1 Feed Pre
RO Stage1
ID004
UF Filtrate Total Chlorine
RO Stage2
RO Stage3
ID301
S3 Conc Pre
S1 Perm Flow
ID302
S3 Conc Flow
ID1000
ID003
S1 Feed Flow
S1_Flow
ID1000
ID003
S1 Feed pH
S2_EC
S2_EC
S2 Perm Flow
ID1000
S2_Flow
ID1000
S3_EC
S3_EC
S3 Perm Flow
ID1000
S3_Flow
ID1000

## Slide 4: Work001 (OCWD) ：最適化変数
Family | ID No. | Description | Var / Param
RO Feed | ID000 | Sulfuric Acid Usage | Opt. Variable
RO Feed | ID001 | Threshold Inhibitor Usage | Opt. Variable
RO Feed | ID002 | Feed Conductivity | Fixed Parameter
RO Feed | ID003 | Feed TOC | Fixed Parameter
RO Feed | ID004 | Feed Temperature | Fixed Parameter
RO Feed | ID005 | Feed pH | Fixed Parameter
RO B01 Stage1 | ID100 | S1 Feed Pressure | Fixed Parameter
RO B01 Stage1 | ID101 | S1 Feed Flow Rate | Fixed Parameter
RO B01 Stage2 | ID200 | S2 Feed Pressure | Fixed Parameter
RO B01 Stage2 | ID201 | S2 Feed Flow Rate | Fixed Parameter
RO B01 Stage3 | ID300 | S3 Feed Flow Rate | Fixed Parameter
Family | ID No. | Description | Var / Param
RO Stage1 | ID1000 | S1 Permeate EC | Intermediate Variable
RO Stage2 | ID2000 | S2 Feed EC | Intermediate Variable
RO Stage2 | ID2001 | S2 Permeate EC | Intermediate Variable
RO Stage3 | ID3000 | S3 Feed EC | Intermediate Variable
RO Stage3 | ID3001 | S3 Permeate EC | Intermediate Variable
RO Total | ID4000 | Permeate TOC | Intermediate Variable

## Slide 5: Work001 (OCWD) ：最適化問題
Lower and Upper limit
Fluctuation range limit
Prediction Model (Black Box)
Output limit (Black Box)
Objective Function
Constraint Conditions
緑：Fixed Parameter
赤：Intermediate Variable

## Slide 6: Work001 (OCWD) ：問題規模
Timestep | Total Opt. Variable | Num of Constraints
48 | 144 | 431
96 | 288 | 863
Timestep | Total Opt. Variable | Num of Constraints
48 | 144 | 431
96 | 288 | 863
Period
  2022/06/01 0:00 – 2022/06/03 0:00
  30min time interval
  97step (first step is all fixed)
Num of Opt. Variable | Num of Param. | Num of Intermediate Variable
3 | 7 | 3

## Slide 7: Work008 (LVMWD) ：フロー図
S1_EC
Sulfuric Acid Dosing
ID000
S1_EC
ID001
ID002
コスト元
S1 Feed EC
S1 Feed TOC
透過TOC予測
TOC
RO Feed
fouling予測
fouling
ID003
S1 Feed Pre
ID200
S2 Perm Flow
RO Total
RO Stage1
ID004
UF Filtrate Total Chlorine
RO Stage2
RO Stage3
ID301
S3 Conc Pre
ID100
S1 Perm Flow
ID302
S3 Conc Flow
ID300
S3 Perm Flow
ID1000
ID1001
ID1002
コスト元

## Slide 8: Work008 (LVMWD) ：最適化変数
Family | ID No. | Description | Tag ID Name | Variable / Param
RO Feed | ID000 | Sulfuric Acid Dosing | RO_Sulfuric_Acid_Dosing_Setpoint | Opt. Variable
RO Feed | ID001 | S1 Feed EC | AIT_40006 | Fixed Parameter
RO Feed | ID002 | S1 Feed TOC | AIT_40010 | Fixed Parameter
RO Feed | ID003 | S1 Feed Pressure | PT_41095 | Fixed Parameter
RO Feed | ID004 | UF Filtrate Total Chlorine | AI_31094 | Opt. Variable
RO Stage1 | ID100 | S1 Permeate Flow Rate | FIT_41074 | Fixed Parameter
RO Stage2 | ID200 | S2 Permeate Flow Rate | FIT_41274 | Fixed Parameter
RO Stage3 | ID300 | S3 Permeate Flow Rate | FIT_41374 | Fixed Parameter
RO Stage3 | ID301 | S3 Concentrate Pressure | PT_41945 | Fixed Parameter
RO Stage3 | ID302 | S3 Concentrate Flow Rate | FIT_41974 | Fixed Parameter
Family | ID No. | Description | Tag ID Name | Variable / Param
RO Stage1 | ID1000 | S1 Permeate EC | AIT_41092 | Intermediate Variable
RO Total | ID1001 | Permeate TOC | AIT_41810 | Intermediate Variable
RO Total | ID1002 | RO Fouling | - | Intermediate Variable

## Slide 9: Work008 (LVMWD) ：最適化問題
Lower and Upper limit
Fluctuation range limit
Prediction Model (Black Box)
Output limit (Black Box)
Objective Function
Constraint Conditions
緑：Fixed Parameter
赤：Intermediate Variable

## Slide 10: Work008 (LVMWD) ：問題規模
Timestep | Total Opt. Variable | Num of Constraints
48 | 96 | 430
96 | 192 | 862
Timestep | Total Opt. Variable | Num of Constraints
48 | 96 | 430
96 | 192 | 862
Period
  2022/06/01 0:00 – 2022/06/02 0:00
  30min time interval
  49step (first step is all fixed)
Num of Opt. Variable | Num of Param. | Num of Intermediate Variable
2 | 8 | 3

## Slide 11: 最適化結果（探索過程における最良解の推移）
2. 最適化結果
制約違反量が0の解を得た。
  ただし、コストには改善の余地がある。

## Slide 12: 最適化結果（操作計画）
2. 最適化結果
コスト元
コスト元
Sulfuric Acid Dosing
UF Filtrate Total Chlorine
S1 Feed EC
S1 Feed TOC
S1 Feed Pre

## Slide 13: 最適化結果（中間変数の予測値）
2. 最適化結果
RO Stage1 permeate EC
RO Total permeate TOC
RO Fouling
征矢さんのモデル
適当なモデル
適当なモデル
本来は0-1に収まるのが正しいが、
実績データなどの選び方のせいで
このくらい緩和した

## Slide 14: 目的関数や最適化変数の議論
目的関数：投入薬品コスト、ポンプ駆動電力コスト、膜交換コスト
短期的（数日）
  最適化：流量はほぼ一定なので圧力は動かさずに、投入薬品だけを変える
  目的関数：投入薬品コスト
  制約：それによって透過水質が基準を維持することが制約
    （LV、EC2/EC1=1.5log,TOC2/TOC1=2log）
長期的（数か月）
  最適化：圧力を動かし、流量が変わる
  目的関数：投入薬品コスト、ポンプ駆動電力コスト、膜交換コスト
  制約：詰まりを解消するように、流量を維持したい（LV、回収率0.8以上）
1. 背景整理